## NSW
GENERAL INPUTS
Display name of asset | Gunnedah supply | OR-BNY line | GW-THA line | TWT-QDI line | OR-ORW line | QBN-Googong line | Beryl TS | Gloucester supply | Blayney ZS | Narrabri TS | Mudgee ZS | Gunnedah TS | Tharbogang ZS | Moree TS | Quirindi ZS | Orange W ZS | Bourkelands ZS
Short name of asset | GUN_NAR_MOR | OR_BNY_STLI | GW_STLI | TQ_STLI | OR_STLI | GTT_STLI | BYL | GLC | BNY | NAR | MUD | GUN | THA | MOR | QDI | ORW | BOU
Full name of asset | Gunnedah-Narrabri- Moree supply | Orange to Blayney - reconductor 66kV feeder | Griffith West - new dual 132kV feeder | Tamworth to Quirindi - new 66kV feeder | Orange N - W feeder | Googong Town to Tralee - new 132 kV feeder | Beryl (aggregate of Beryl, Mudgee and Ilford) | STR4B6 Gloucester No | Blayney ZS | Narrabri Terminal Substation | Mudgee zone substation | Gunnedah Terminal Substation | THARBOGANG 33/11 | Moree Terminal Substation | Quirindi ZS | ORANGE WEST 66/11 | Bourkelands
Region | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW | NSW
Asset type | Stli | Stli | Stli | Stli | Stli | Stli | TS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS
Provider | Transgrid | Essential | Essential | Essential | Essential | Essential | Transgrid | Essential | Essential | Transgrid | Essential | Transgrid | Essential | Transgrid | Essential | Essential | Essential
Associated Tx | [10 empty] | BYL
Associated STL | [8 empty] | OR_BNY_STLI | GUN_NAR_MOR |  | GUN_NAR_MOR | GW_STLI | GUN_NAR_MOR | TQ_STLI | OR_STLI
Latitude | -30.9774 | -33.5663 | -34.2816 | -31.4942 | -33.2844 | -33.4332 | -32.3483 | -32.0141 | -33.5663 | -30.317 | -32.5861 | -30.9774 | -34.2816 | -29.4852 | -31.4942 | -33.2684 | -35.155
Longitude | 150.3397 | 148.9891 | 146.0019 | 150.6785 | 149.0858 | 149.2078 | 149.4611 | 151.9652 | 148.9891 | 149.7976 | 149.5692 | 150.3397 | 146.0019 | 149.8555 | 150.6785 | 149.0722 | 147.3422
POE value |  | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown |  | Unknown |  | Unknown |  | Unknown | Unknown | Unknown
Season to use
Land available | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Notes for outputsheet | New supply to Gunnedah-Moree-Narrabri area. Assumes 2 hot spots. | Blaney area supplied at 66kV from Bathurst. Existing load approaching 15kV with projected increase associated with mining. Should this eventuate & N-1 reliability be required, alternative 66kV feed from Orange would need to be augmented. |  |  |  |  | This is aggregaate demand for Transgrid & Essential loads at Beryl, Mudgee & Ilford. | Load & forecast for GLC AREA, not ZS used. Existing 33kV network has N-1 capacity of 19.5MVA. Current peak demand ~12MVA & new 7MVA mining load projected. Unacceptable overload in N-1 conditions. |  | Voltage support required for supply to Gunnedah-Moree-Narrabri area; 80% value if provided here |  | Voltage support required for supply to Gunnedah-Moree-Narrabri area; 100% value if provided here |  | Voltage support required for supply to Gunnedah-Moree-Narrabri area; 80% value if provided here |  |  | Peak demand on ZS expected to exceed summer rating in 2017/18
Maximum connection | 95 | 17.96 | 15 | 18.6429 |  |  | 95 | 19.5 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
NETWORK INVESTMENT
Proposed investment ($m) | 30 | 8 | 4.5 | 20 | 1.1 | 4.3 | 35 | 15.7 |  |  | 1.5 | [5 empty] | 2
Proposed investment year | 2019 | 2016 | 2015 | 2017 | 2016 | 2018 | 2016 | 2016 |  |  | 2019 | [5 empty] | 2018
Annual Deferral Value of system in 2014 ($/kVA/yr) | 102745.4712 | 661.8312 | 4680.4907 | 1338.8001 |  |  | 583.2387 | 646.67 | 661.8312 | 102745.4712 | 1535.4318 | 102745.4712 | 4680.4907 | 102745.4712 | 1338.8001 |  | 125.7835
Type of constraint | Growth, Voltage | Growth - mine related | Growth | Growth - mine related |  |  | Voltage | Growth - mine related |  | None, Voltage | Reliability | None, Voltage | Growth | None, Voltage |  |  | Growth
Constraint season | BOTH | Winter | Winter | Summer |  |  | BOTH (Summer) | Summer |  |  | BOTH (Winter) | [5 empty] | Summer
Capacity Shortfall: INVEST YEAR (MVA) | 35 | 0.94 | 0.08 | 1.0857 |  |  | 7 | 1.888 |  | - | 2.4 | - | - | - |  |  | 0.91667
Capacity Shortfall: Year 10 (MVA) | 42.4932 | 5.74 | 0.58 | 7.7714 |  |  | 36.3333 | 14.173 |  | - | 3.2 | - | - | - |  |  | 7.7333
SYSTEM INVESTMENT
Investment for system ($m) | 30 | 8 | 4.5 | 20 | 1.1 | 4.3 | 35 | 15.7 | 8 | 30 | 36.5 | 30 | 4.5 | 30 | 20 | 1.1 | 2
Investment for ZS ($m) | [7 empty] | 15.7 |  |  | 1.5 | [5 empty] | 2
Investment for Stli ($m) | 30 | 8 | 4.5 | 20 | 1.1 | 4.3 |  |  | 8 | 30 |  | 30 | 4.5 | 30 | 20 | 1.1
Investment for TS ($m) | [6 empty] | 35 |  |  |  | 35
Investment year for system | 2019 | 2016 | 2015 | 2017 | 2016 | 2018 | 2016 | 2016 | 2016 | 2019 | 2016 | 2019 | 2015 | 2019 | 2017 | 2016 | 2018
Investment year for ZS | [7 empty] | 2016 |  |  | 2019 | [5 empty] | 2018
Investment year for Stli | 2019 | 2016 | 2015 | 2017 | 2016 | 2018 |  |  | 2016 | 2019 |  | 2019 | 2015 | 2019 | 2017 | 2016
Investment year for TS | [6 empty] | 2016 |  |  |  | 2016
System capacity shortfall: INVEST YEAR (MVA) | 35 | 0.94 | 0.08 | 1.0857 |  |  | 7 | 1.888 | 0.94 | 35 | 7 | 35 | 0.08 | 35 | 1.0857 |  | 0.91667
ZS capacity shortfall: INVEST YEAR (MVA) | [7 empty] | 1.888 |  | - | 2.4 | - | - | - |  |  | 0.91667
Stli capacity shortfall: INVEST YEAR (MVA) | 35 | 0.94 | 0.08 | 1.0857 |  |  |  |  | 0.94 | 35 |  | 35 | 0.08 | 35 | 1.0857
TS capacity shortfall: INVEST YEAR (MVA) | [6 empty] | 7 |  |  |  | 7
System capacity shortfall: Year 10 (MVA) | 42.4932 | 5.74 | 0.58 | 7.7714 |  |  | 36.3333 | 14.173 | 5.74 | 42.4932 | 36.3333 | 42.4932 | 0.58 | 42.4932 | 7.7714 |  | 7.7333
ZS capacity shortfall: Year 10 (MVA) | [7 empty] | 14.173 |  | - | 3.2 | - | - | - |  |  | 7.7333
Stli capacity shortfall: Year 10 (MVA) | 42.4932 | 5.74 | 0.58 | 7.7714 |  |  |  |  | 5.74 | 42.4932 |  | 42.4932 | 0.58 | 42.4932 | 7.7714
TS capacity shortfall: Year 10 (MVA) | [6 empty] | 36.3333 |  |  |  | 36.3333
NET PRESENT VALUE IN 2014 ($m)
of system | 27.903 | 6.6651 | 3.5829 | 17.3534 | 0.91646 | 3.8697 | 29.16 | 13.0803 | 6.6651 | 27.903 | 30.5551 | 27.903 | 3.5829 | 27.903 | 17.3534 | 0.91646 | 1.7999
of asset | 27.903 | 6.6651 | 3.5829 | 17.3534 | 0.91646 | 3.8697 | 29.16 | 13.0803 |  |  | 1.3951 | [5 empty] | 1.7999
of linked ZS | [7 empty] | 13.0803 |  |  | 1.3951 | [5 empty] | 1.7999
of linked Stli | 27.903 | 6.6651 | 3.5829 | 17.3534 | 0.91646 | 3.8697 |  |  | 6.6651 | 27.903 |  | 27.903 | 3.5829 | 27.903 | 17.3534 | 0.91646
of linked TS | [6 empty] | 29.16 |  |  |  | 29.16
AVAILABLE CAPACITY (MVA)
2010 | 0.14828 | 5.64 | 0.48 | 6.5143 |  |  | 21 | 5.352 |  |  | -1.6 | [5 empty] | 6.7433
2011 | 0.12974 | 4.7 | 0.4 | 2.6429 |  |  | 16.3333 | 4.652 |  |  | -1.7 | [5 empty] | 2.6833
2012 | 0.11121 | 3.76 | 0.32 | 4.3429 |  |  | 11.6667 | 7.452 |  |  | -1.8 | [5 empty] | 4.5833
2013 | 0.092675 | 4.46 | 0.32 | 3.3429 |  |  | 7 | 4.922 |  |  | -2.3 | [5 empty] | -0.21667
2014 | 0.07414 | 4.16 | 0.02 | 2.0429 |  |  | -1 | 4.822 |  |  | -1.4 | [5 empty] | -0.31667
2015 | 0.055605 | 4.06 | -0.08 | 2 |  |  | -7 | -1.588 |  |  | -2.2 | [5 empty] | -0.51667
2016 | 0.03707 | -0.94 | -0.08 | -1.0429 |  |  | -7 | -1.888 |  |  | -2.3 | [5 empty] | -0.61667
2017 | 0.018535 | -0.94 | -0.08 | -1.0857 |  |  | -8 | -1.988 |  |  | -2.3 | [5 empty] | -0.81667
2018 | - | -0.94 | -0.08 | -1.1286 |  |  | -10 | -2.088 |  |  | -2.4 | [5 empty] | -0.91667
2019 | -35 | -0.94 | -0.08 | -1.1714 |  |  | -11 | -2.188 |  |  | -2.4 | [5 empty] | -1.0167
2020 | -36 | -1.04 | -0.18 | -1.2143 |  |  | -12 | -2.388 |  |  | -2.5 | [5 empty] | -1.2167
2021 | -39.144 | -1.04 | -0.18 | -1.2571 |  |  | -13 | -2.498 |  |  | -2.5 | [5 empty] | -1.3167
2022 | -42.3635 | -1.04 | -0.18 | -6.5143 |  |  | -35 | -13.663 |  |  | -2.6 | [5 empty] | -5.4
ANNUAL DEFERRAL VALUES or ADV
ADV OF Asset ($/kVA/year)
2010 | 78384.0281 | 504.9078 | 3570.7239 | 1021.3642 |  |  | 444.95 | 493.3415 |  |  | 726.4235 | [5 empty] | 95.9596
2011 | 83870.91 | 540.2514 | 3820.6746 | 1092.8597 |  |  | 476.0965 | 527.8754 |  |  | 777.2732 | [5 empty] | 102.6768
2012 | 89741.8737 | 578.069 | 4088.1218 | 1169.3599 |  |  | 509.4233 | 564.8267 |  |  | 831.6823 | [5 empty] | 109.8642
2013 | 96023.8049 | 618.5338 | 4374.2903 | 1251.2151 |  |  | 545.0829 | 604.3645 |  |  | 889.9 | [5 empty] | 117.5547
2014 | 102745.4712 | 661.8312 | 4680.4907 | 1338.8001 |  |  | 583.2387 | 646.67 |  |  | 952.193 | [5 empty] | 125.7835
2015 | 109937.6542 | 708.1593 | 5008.125 | 1432.5161 |  |  | 624.0654 | 691.9369 |  |  | 1018.8466 | [5 empty] | 134.5884
2016 | 117633.29 | 757.7305 | - | 1532.7923 |  |  | 667.75 | 740.3725 |  |  | 1090.1658 | [5 empty] | 144.0096
2017 | 125867.6203 | - | - | 1640.0877 |  |  | - | - |  |  | 1166.4774 | [5 empty] | 154.0902
2018 | 134678.3537 | - | - | - |  |  | - | - |  |  | 2080.2181 | [5 empty] | 194.2545
2019 | 144105.8385 | - | - | - |  |  | - | - |  |  | 2225.8333 | [5 empty] | -
2020 | - | - | - | - |  |  | - | - |  |  | - | [5 empty] | -
2021 | - | - | - | - |  |  | - | - |  |  | - | [5 empty] | -
2022 | - | - | - | - |  |  | - | - |  |  | - | [5 empty] | -
ADV OF LINKED Stli ($/kVA/year)
2010 | 78384.0281 | 504.9078 | 3570.7239 | 1021.3642 |  |  |  |  | 504.9078 | 78384.0281 |  | 78384.0281 | 3570.7239 | 78384.0281 | 1021.3642
2011 | 83870.91 | 540.2514 | 3820.6746 | 1092.8597 |  |  |  |  | 540.2514 | 83870.91 |  | 83870.91 | 3820.6746 | 83870.91 | 1092.8597
2012 | 89741.8737 | 578.069 | 4088.1218 | 1169.3599 |  |  |  |  | 578.069 | 89741.8737 |  | 89741.8737 | 4088.1218 | 89741.8737 | 1169.3599
2013 | 96023.8049 | 618.5338 | 4374.2903 | 1251.2151 |  |  |  |  | 618.5338 | 96023.8049 |  | 96023.8049 | 4374.2903 | 96023.8049 | 1251.2151
2014 | 102745.4712 | 661.8312 | 4680.4907 | 1338.8001 |  |  |  |  | 661.8312 | 102745.4712 |  | 102745.4712 | 4680.4907 | 102745.4712 | 1338.8001
2015 | 109937.6542 | 708.1593 | 5008.125 | 1432.5161 |  |  |  |  | 708.1593 | 109937.6542 |  | 109937.6542 | 5008.125 | 109937.6542 | 1432.5161
2016 | 117633.29 | 757.7305 | - | 1532.7923 |  |  |  |  | 757.7305 | 117633.29 |  | 117633.29 | - | 117633.29 | 1532.7923
2017 | 125867.6203 | - | - | 1640.0877 |  |  |  |  | - | 125867.6203 |  | 125867.6203 | - | 125867.6203 | 1640.0877
2018 | 134678.3537 | - | - | - |  |  |  |  | - | 134678.3537 |  | 134678.3537 | - | 134678.3537 | -
2019 | 144105.8385 | - | - | - |  |  |  |  | - | 144105.8385 |  | 144105.8385 | - | 144105.8385 | -
2020 | - | - | - | - |  |  |  |  | - | - |  | - | - | - | -
2021 | - | - | - | - |  |  |  |  | - | - |  | - | - | - | -
2022 | - | - | - | - |  |  |  |  | - | - |  | - | - | - | -
ADV OF LINKED TS ($/kVA/year)
2010 | [6 empty] | 444.95 |  |  |  | 444.95
2011 | [6 empty] | 476.0965 |  |  |  | 476.0965
2012 | [6 empty] | 509.4233 |  |  |  | 509.4233
2013 | [6 empty] | 545.0829 |  |  |  | 545.0829
2014 | [6 empty] | 583.2387 |  |  |  | 583.2387
2015 | [6 empty] | 624.0654 |  |  |  | 624.0654
2016 | [6 empty] | 667.75 |  |  |  | 667.75
2017 | [6 empty] | - |  |  |  | -
2018 | [6 empty] | - |  |  |  | -
2019 | [6 empty] | - |  |  |  | -
2020 | [6 empty] | - |  |  |  | -
2021 | [6 empty] | - |  |  |  | -
2022 | [6 empty] | - |  |  |  | -
ADV OF SYSTEM ($/kVA/year)
2010 | 78384.0281 | 504.9078 | 3570.7239 | 1021.3642 |  |  | 444.95 | 493.3415 | 504.9078 | 78384.0281 | 1171.3735 | 78384.0281 | 3570.7239 | 78384.0281 | 1021.3642 |  | 95.9596
2011 | 83870.91 | 540.2514 | 3820.6746 | 1092.8597 |  |  | 476.0965 | 527.8754 | 540.2514 | 83870.91 | 1253.3697 | 83870.91 | 3820.6746 | 83870.91 | 1092.8597 |  | 102.6768
2012 | 89741.8737 | 578.069 | 4088.1218 | 1169.3599 |  |  | 509.4233 | 564.8267 | 578.069 | 89741.8737 | 1341.1056 | 89741.8737 | 4088.1218 | 89741.8737 | 1169.3599 |  | 109.8642
2013 | 96023.8049 | 618.5338 | 4374.2903 | 1251.2151 |  |  | 545.0829 | 604.3645 | 618.5338 | 96023.8049 | 1434.9829 | 96023.8049 | 4374.2903 | 96023.8049 | 1251.2151 |  | 117.5547
2014 | 102745.4712 | 661.8312 | 4680.4907 | 1338.8001 |  |  | 583.2387 | 646.67 | 661.8312 | 102745.4712 | 1535.4318 | 102745.4712 | 4680.4907 | 102745.4712 | 1338.8001 |  | 125.7835
2015 | 109937.6542 | 708.1593 | 5008.125 | 1432.5161 |  |  | 624.0654 | 691.9369 | 708.1593 | 109937.6542 | 1642.912 | 109937.6542 | 5008.125 | 109937.6542 | 1432.5161 |  | 134.5884
2016 | 117633.29 | 757.7305 | - | 1532.7923 |  |  | 667.75 | 740.3725 | 757.7305 | 117633.29 | 1757.9158 | 117633.29 | - | 117633.29 | 1532.7923 |  | 144.0096
2017 | 125867.6203 | - | - | 1640.0877 |  |  | - | - | - | 125867.6203 | 1166.4774 | 125867.6203 | - | 125867.6203 | 1640.0877 |  | 154.0902
2018 | 134678.3537 | - | - | - |  |  | - | - | - | 134678.3537 | 2080.2181 | 134678.3537 | - | 134678.3537 | - |  | 194.2545
2019 | 144105.8385 | - | - | - |  |  | - | - | - | 144105.8385 | 2225.8333 | 144105.8385 | - | 144105.8385 | - |  | -
2020 | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - |  | -
2021 | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - |  | -
2022 | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - |  | -
HOURLY EXCEEDANCES: INVEST YEAR
Investment trigger point (MVA) | 95 | 17.96 | 17.32 | 18.6429 |  |  | 95 | 20.052 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
Year | 2019 | 2016 | 2015 | 2017 |  |  | 2016 | 2016 |  |  | 2019 | [5 empty] | 2018
No. of hours over the trigger point (hr) | 521 | [5 empty] | 12 |  |  |  | 112
Duration of Exceedance by Month INVEST YEAR (total number of hours on worst day) (hr)
January | 8 | [5 empty] | - |  |  |  | -
February | - | [5 empty] | - |  |  |  | -
March | - | [5 empty] | - |  |  |  | -
April | - | [5 empty] | - |  |  |  | -
May | 3 | [5 empty] | - |  |  |  | 2
June | 21 | [5 empty] | 4 |  |  |  | 3
July | 4 | [5 empty] | - |  |  |  | 3
August | - | [5 empty] | - |  |  |  | 4
September | - | [5 empty] | - |  |  |  | 1
October | - | [5 empty] | - |  |  |  | -
November | 14 | [5 empty] | - |  |  |  | -
December | 14 | [5 empty] | - |  |  |  | -
Duration of Exceedance by Month INVEST YEAR (number of consecuative hours on worst day) (hr)
January | 8 | [5 empty] | - |  |  |  | -
February | - | [5 empty] | - |  |  |  | -
March | - | [5 empty] | - |  |  |  | -
April | - | [5 empty] | - |  |  |  | -
May | 3 | [5 empty] | - |  |  |  | 2
June | 18 | [5 empty] | 3 |  |  |  | 3
July | 2 | [5 empty] | - |  |  |  | 3
August | - | [5 empty] | - |  |  |  | 3
September | - | [5 empty] | - |  |  |  | 1
October | - | [5 empty] | - |  |  |  | -
November | 14 | [5 empty] | - |  |  |  | -
December | 14 | [5 empty] | - |  |  |  | -
MAX EXCEEDANCE BY MONTH: INVEST YEAR (MVA)
January | 8.4643 | [5 empty] | - |  |  |  | -
February | - | [5 empty] | - |  |  |  | -
March | - | [5 empty] | - |  |  |  | -
April | - | [5 empty] | - |  |  |  | -
May | 8.5896 | [5 empty] | - |  |  |  | 0.6573
June | 35 | [5 empty] | 7 |  |  |  | 1.7581
July | 11.6934 | [5 empty] | - |  |  |  | 2.4
August | - | [5 empty] | - |  |  |  | 2.1558
September | - | [5 empty] | - |  |  |  | 0.22276
October | - | [5 empty] | - |  |  |  | -
November | 22.2982 | [5 empty] | - |  |  |  | -
December | 25.1215 | [5 empty] | - |  |  |  | -
Number of days of Exceedance by Month: INVEST YEAR (days)
January | 9 | [5 empty] | - |  |  |  | -
February | - | [5 empty] | - |  |  |  | -
March | - | [5 empty] | - |  |  |  | -
April | - | [5 empty] | - |  |  |  | -
May | 11 | [5 empty] | - |  |  |  | 2
June | 26 | [5 empty] | 5 |  |  |  | 12
July | 13 | [5 empty] | - |  |  |  | 22
August | - | [5 empty] | - |  |  |  | 20
September | - | [5 empty] | - |  |  |  | 3
October | - | [5 empty] | - |  |  |  | -
November | 14 | [5 empty] | - |  |  |  | -
December | 14 | [5 empty] | - |  |  |  | -
HOURLY EXCEEDANCES: Year 10
Investment trigger point (MVA) | 95 | 17.96 | 17.32 | 18.6429 |  |  | 95 | 20.052 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
Year | 2029 | 2026 | 2025 | 2027 |  |  | 2026 | 2026 |  |  | 2029 | [5 empty] | 2028
No. of hours over the trigger point (hr) | 842 | [5 empty] | 957 |  |  |  | 216
Duration of Exceedance by Month Year 10 (total number of hours on worst day) (hr)
January | 10 | [5 empty] | 8 |  |  |  | -
February | 3 | [5 empty] | 3 |  |  |  | -
March | - | [5 empty] | 1 |  |  |  | -
April | - | [5 empty] | 3 |  |  |  | -
May | 8 | [5 empty] | 10 |  |  |  | 2
June | 21 | [5 empty] | 24 |  |  |  | 5
July | 8 | [5 empty] | 18 |  |  |  | 5
August | 1 | [5 empty] | 12 |  |  |  | 7
September | - | [5 empty] | 7 |  |  |  | 2
October | - | [5 empty] | 1 |  |  |  | 1
November | 16 | [5 empty] | 13 |  |  |  | -
December | 15 | [5 empty] | 13 |  |  |  | -
Duration of Exceedance by Month Year 10 (number of consecuative hours on worst day) (hr)
January | 10 | [5 empty] | 8 |  |  |  | -
February | 2 | [5 empty] | 3 |  |  |  | -
March | - | [5 empty] | 1 |  |  |  | -
April | - | [5 empty] | 2 |  |  |  | -
May | 4 | [5 empty] | 6 |  |  |  | 2
June | 18 | [5 empty] | 24 |  |  |  | 4
July | 4 | [5 empty] | 8 |  |  |  | 4
August | 1 | [5 empty] | 7 |  |  |  | 3
September | - | [5 empty] | 5 |  |  |  | 1
October | - | [5 empty] | 1 |  |  |  | 1
November | 16 | [5 empty] | 13 |  |  |  | -
December | 15 | [5 empty] | 13 |  |  |  | -
MAX EXCEEDANCE BY MONTH: Year 10 (MVA)
January | 14.4279 | [5 empty] | 11.548 |  |  |  | -
February | 1.142 | [5 empty] | 3.6866 |  |  |  | -
March | - | [5 empty] | 0.51351 |  |  |  | -
April | - | [5 empty] | 9.6848 |  |  |  | -
May | 14.5605 | [5 empty] | 19.8218 |  |  |  | 1.3922
June | 42.4932 | [5 empty] | 36.3333 |  |  |  | 2.5341
July | 17.8432 | [5 empty] | 25.7737 |  |  |  | 3.2
August | 0.094711 | [5 empty] | 22.5503 |  |  |  | 2.9466
September | - | [5 empty] | 14.4696 |  |  |  | 0.94137
October | - | [5 empty] | 5.3486 |  |  |  | 0.70593
November | 29.0593 | [5 empty] | 26.3975 |  |  |  | -
December | 32.0453 | [5 empty] | 19.1317 |  |  |  | -
Number of days of Exceedance by Month: Year 10 (days)
January | 12 | [5 empty] | 9 |  |  |  | -
February | 5 | [5 empty] | 1 |  |  |  | -
March | - | [5 empty] | 2 |  |  |  | -
April | - | [5 empty] | 5 |  |  |  | -
May | 16 | [5 empty] | 24 |  |  |  | 8
June | 30 | [5 empty] | 30 |  |  |  | 21
July | 17 | [5 empty] | 28 |  |  |  | 29
August | 2 | [5 empty] | 25 |  |  |  | 24
September | - | [5 empty] | 16 |  |  |  | 4
October | - | [5 empty] | 1 |  |  |  | 1
November | 15 | [5 empty] | 10 |  |  |  | -
December | 16 | [5 empty] | 7 |  |  |  | -
LOAD PROFILE: INVEST YEAR (MVA)
Year | 2019 | 2016 | 2015 | 2017 |  |  | 2016 | 2016 |  |  | 2019 | [5 empty] | 2018
Peak load (MVA) | 130 | 18.9 | 17.4 | 19.7286 |  |  | 102 | 21.94 |  |  | 21.4 | [5 empty] | 14.4
Investment trigger point (MVA) | 95 | 17.96 | 17.32 | 18.6429 |  |  | 95 | 20.052 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
PEAK DAY LOAD PROFILE: INVEST YEAR (MVA)
12 am | 106.0606 | [5 empty] | 65.9153 |  |  |  | 11.2895
1 am | 106.636 | [5 empty] | 65.8028 |  |  |  | 10.5817
2 am | 98.3904 | [5 empty] | 64.176 |  |  |  | 9.8973
3 am | 84.8423 | [5 empty] | 63.6572 |  |  |  | 9.6674
4 am | 83.8348 | [5 empty] | 63.826 |  |  |  | 9.8741
5 am | 88.072 | [5 empty] | 66.517 |  |  |  | 10.3209
6 am | 102.8019 | [5 empty] | 70.9535 |  |  |  | 11.3289
7 am | 119.1642 | [5 empty] | 76.1996 |  |  |  | 13.4162
8 am | 122.3714 | [5 empty] | 78.6265 |  |  |  | 16.3451
9 am | 116.2802 | [5 empty] | 77.6123 |  |  |  | 16.6185
10 am | 110.772 | [5 empty] | 76.1871 |  |  |  | 15.6984
11 am | 105.6449 | [5 empty] | 72.6663 |  |  |  | 15.1585
12 pm | 101.4075 | [5 empty] | 70.6363 |  |  |  | 14.7624
1 pm | 97.9395 | [5 empty] | 70.9285 |  |  |  | 14.0725
2 pm | 95.5736 | [5 empty] | 75.4417 |  |  |  | 14.4677
3 pm | 96.7759 | [5 empty] | 74.8478 |  |  |  | 14.8218
4 pm | 100.5523 | [5 empty] | 82.8161 |  |  |  | 16.4147
5 pm | 116.8458 | [5 empty] | 98.8886 |  |  |  | 20.5263
6 pm | 130 | [5 empty] | 102 |  |  |  | 21.4
7 pm | 124.791 | [5 empty] | 98.5964 |  |  |  | 20.3362
8 pm | 117.7105 | [5 empty] | 87.984 |  |  |  | 18.5914
9 pm | 110.276 | [5 empty] | 90.8094 |  |  |  | 16.5252
10 pm | 110.9157 | [5 empty] | 96.1758 |  |  |  | 14.3206
11 pm | 109.3599 | [5 empty] | 89.1107 |  |  |  | 12.7999
LOAD PROFILE: Year 10 (MVA)
Year | 2029 | 2026 | 2025 | 2027 |  |  | 2026 | 2026 |  |  | 2029 | [5 empty] | 2028
Peak load (MVA) | 137.4932 | 23.7 | 17.9 | 26.4143 |  |  | 131.3333 | 34.225 |  |  | 22.2 | [5 empty] | 21.2167
Investment trigger point (MVA) | 95 | 17.96 | 17.32 | 18.6429 |  |  | 95 | 20.052 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
PEAK DAY LOAD PROFILE: Year 10 (MVA)
12 am | 112.1739 | [5 empty] | 84.8714 |  |  |  | 11.7115
1 am | 112.7825 | [5 empty] | 84.7265 |  |  |  | 10.9773
2 am | 104.0616 | [5 empty] | 82.6319 |  |  |  | 10.2673
3 am | 89.7326 | [5 empty] | 81.9639 |  |  |  | 10.0288
4 am | 88.667 | [5 empty] | 82.1812 |  |  |  | 10.2432
5 am | 93.1485 | [5 empty] | 85.6461 |  |  |  | 10.7068
6 am | 108.7274 | [5 empty] | 91.3585 |  |  |  | 11.7524
7 am | 126.0328 | [5 empty] | 98.1132 |  |  |  | 13.9178
8 am | 129.4249 | [5 empty] | 101.238 |  |  |  | 16.9561
9 am | 122.9825 | [5 empty] | 99.9321 |  |  |  | 17.2398
10 am | 117.1569 | [5 empty] | 98.0971 |  |  |  | 16.2853
11 am | 111.7343 | [5 empty] | 93.5638 |  |  |  | 15.7252
12 pm | 107.2526 | [5 empty] | 90.95 |  |  |  | 15.3143
1 pm | 103.5848 | [5 empty] | 91.3263 |  |  |  | 14.5985
2 pm | 101.0825 | [5 empty] | 97.1373 |  |  |  | 15.0086
3 pm | 102.3541 | [5 empty] | 96.3727 |  |  |  | 15.3759
4 pm | 106.3482 | [5 empty] | 106.6325 |  |  |  | 17.0283
5 pm | 123.5808 | [5 empty] | 127.3272 |  |  |  | 21.2937
6 pm | 137.4932 | [5 empty] | 131.3333 |  |  |  | 22.2
7 pm | 131.984 | [5 empty] | 126.9509 |  |  |  | 21.0964
8 pm | 124.4953 | [5 empty] | 113.2866 |  |  |  | 19.2864
9 pm | 116.6323 | [5 empty] | 116.9245 |  |  |  | 17.143
10 pm | 117.3089 | [5 empty] | 123.8341 |  |  |  | 14.8559
11 pm | 115.6634 | [5 empty] | 114.7373 |  |  |  | 13.2784
SUMMER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 95 | 14.94 | 12 | 18.6429 |  |  | 95 | 19.5 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
n-1 capacity (MVA) | 95 | 14.94 | 12 | 18.6429 |  |  | 95 | 19.5 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
Secure capacity (MVA) | 95 | 14.94 | 12 | 18.6429 |  |  | 95 | 19.5 |  | 60 | 19 | 60 | 12 | 60 |  |  | 13.4833
Reliability requirement | N-1 |  | N-1 | [6 empty] | N-1 |  | N-1 | N | N-1 |  | N-1
Actual/forecast peak load: Summer (MVA)
2010 | 94.8517 | 10.98 | 15.88 | 12.1286 |  |  | 74 | 14.7 | 9.88 | 55.6562 | 17.4 | 27.1067 | 15.74 | 27.4018 |  | 11.22 | 6.74
2011 | 94.8703 | 12.2 | 15.9 | 16 |  |  | 78.6667 | 15.4 | 9.9 | 56.3943 | 22.2 | 27.4579 | 15.9 | 27.8885 |  | 9.9 | 10.8
2012 | 94.8888 | 12.3 | 16 | 14.3 |  |  | 83.3333 | 12.6 | 10 | 57.1324 | 18.2 | 27.8091 | 15.9 | 28.3751 |  | 11.1 | 8.9
2013 | 94.9073 | 12.5 | 16.2 | 15.3 |  |  | 88 | 15.13 | 10.2 | 57.8705 | 20 | 28.1603 | 16 | 28.8617 |  | 10.8 | 13.7
2014 | 94.9259 | 12.5 | 16.2 | 16.6 |  |  | 96 | 15.23 | 10.2 | 57.8705 | 20 | 29.1204 | 16 | 29.8329 |  | 10.8 | 13.8
2015 | 94.9444 | 12.5 | 16.2 | 16.6429 |  |  | 102 | 21.64 | 10.2 | 58.8218 | 20.1 | 29.1204 | 16.1 | 29.8329 |  | 10.8 | 14
2016 | 94.9629 | 15.6 | 16.3 | 19.6857 |  |  | 102 | 21.94 | 10.3 | 60.0833 | 20.2 | 29.1204 | 16.2 | 29.8329 |  | 10.8 | 14.1
2017 | 94.9815 | 15.6 | 16.3 | 19.7286 |  |  | 103 | 22.04 | 10.3 | 60.0833 | 20.2 | 30.0832 | 16.3 | 29.8329 |  | 10.8 | 14.3
2018 | 95 | 15.6 | 16.3 | 19.7714 |  |  | 105 | 22.14 | 10.3 | 61.0328 | 20.3 | 30.0832 | 16.4 | 30.8058 |  | 10.8 | 14.4
2019 | 130 | 15.6 | 16.3 | 19.8143 |  |  | 106 | 22.24 | 10.3 | 61.9839 | 20.4 | 30.3645 | 16.4 | 31.0483 |  | 10.8 | 14.5
2020 | 131 | 15.6 | 16.3 | 19.8571 |  |  | 107 | 22.44 | 10.3 | 61.9839 | 20.4 | 31.3209 | 16.5 | 31.0483 |  | 10.8 | 14.7
2021 | 134.144 | 15.7 | 16.4 | 19.9 |  |  | 108 | 22.55 | 10.4 | 63.2456 | 20.5 | 31.3209 | 16.5 | 32.0156 |  | 10.8 | 14.8
2022 | 137.3635 | 19.725 | 16.6333 | 25.1571 |  |  | 130 | 33.715 | 10.5222 | 64.5136 | 21.7714 | 31.3209 | 16.6333 | 33.2415 |  | 10.6333 | 18.8833
Average Growth (MVA/yr)
2012 to 2017 | 0.018535 | 0.66 | 0.06 | 1.0857 |  |  | 4.6667 | 1.888 | 0.06 | 0.73811 | 0.4 | 0.35118 | 0.08 | 0.48664 |  | -0.06 | 1.08
2017 to 2022 | 0.018535 | 0.825 | 0.066667 | 1.0857 |  |  | 4.6667 | 2.335 | 0.044444 | 0.88606 | 0.31429 | 0.24754 | 0.066667 | 0.68173 |  | -0.033333 | 0.91667
2022 onwards | 0.018535 | 0.825 | 0.066667 | 1.0857 |  |  | 4.6667 | 2.335 | 0.044444 | 0.73811 | 0.31429 | 0.35118 | 0.066667 | 0.48664 |  | -0.033333 | 0.91667
WINTER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 113 | 17.96 | 15 |  |  |  | 100 |  |  |  | 19 |  | 12 |  |  |  | 11.26
n-1 capacity (MVA) | 113 | 17.96 | 15 |  |  |  | 100 |  |  |  | 19 |  | 12 |  |  |  | 11.26
Secure capacity (MVA) | 113 | 17.96 | 15 |  |  |  | 100 |  |  |  | 19 |  | 12 |  |  |  | 11.26
Reliability requirement |  |  | N-1 | [9 empty] | N |  |  | N-1
Actual/forecast peak load: Winter (MVA)
2010 | 112.936 | 12.32 | 16.84 |  |  |  | 62 |  | 11.82 | 56.1875 | 20.6 | 26.13 | 10.1 | 36.3793 |  | 13.88 | 8.12
2011 | 112.944 | 13.26 | 16.92 |  |  |  | 69 |  | 11.76 | 56.8548 | 20.7 | 26.2769 | 10.1 | 36.6222 |  | 13.94 | 8.56
2012 | 112.952 | 14.2 | 17 |  |  |  | 76 |  | 11.7 | 57.522 | 20.8 | 26.4238 | 10.1 | 36.8651 |  | 14 | 9
2013 | 112.96 | 13.5 | 17 |  |  |  | 83 |  | 11 | 58.1893 | 21.3 | 26.5707 | 9.1 | 37.108 |  | 13.1 | 8.6
2014 | 112.968 | 13.8 | 17.3 |  |  |  | 90 |  | 11.3 | 58.1893 | 20.4 | 25.7099 | 10.3 | 37.108 |  | 14.4 | 10.1
2015 | 112.976 | 13.9 | 17.4 |  |  |  | 103 |  | 11.4 | 58.1893 | 21.2 | 26.6833 | 9.9 | 38.0789 |  | 14.1 | 11
2016 | 112.984 | 18.9 | 17.4 |  |  |  | 104 |  | 11.4 | 58.1893 | 21.3 | 26.6833 | 10 | 38.0789 |  | 14.2 | 11.1
2017 | 112.992 | 18.9 | 17.4 |  |  |  | 105 |  | 11.4 | 63.2456 | 21.3 | 26.9258 | 10.1 | 38.0789 |  | 14.3 | 11.2
2018 | 113 | 18.9 | 17.4 |  |  |  | 106 |  | 11.4 | 64.195 | 21.4 | 26.9258 | 10.2 | 38.0789 |  | 14.3 | 11.4
2019 | 133 | 18.9 | 17.4 |  |  |  | 107 |  | 11.4 | 64.195 | 21.4 | 27.8927 | 10.2 | 39.0512 |  | 14.4 | 11.5
2020 | 134.064 | 19 | 17.5 |  |  |  | 108 |  | 11.5 | 64.195 | 21.5 | 27.8927 | 10.3 | 39.0512 |  | 14.5 | 11.6
2021 | 135.1365 | 19 | 17.5 |  |  |  | 108 |  | 11.5 | 64.195 | 21.5 | 27.8927 | 10.4 | 39.2938 |  | 14.6 | 11.8
2022 | 136.2176 | 19 | 17.5 |  |  |  | 109 |  | 11.5 | 64.195 | 21.6 | 27.8927 | 10.4 | 39.2938 |  | 14.6 | 11.9
Average Growth (MVA/yr)
2012 to 2017 | 0.008 | 0.94 | 0.08 |  |  |  | 7 |  | -0.06 | 0.6673 | 0.1 | 0.14689 | - | 0.24287 |  | 0.06 | 0.44
2017 to 2022 | 0.008 | 0.02 | 0.02 |  |  |  | 0.8 |  | 0.02 | 0.18989 | 0.06 | 0.19337 | 0.06 | 0.24298 |  | 0.06 | 0.14
2022 onwards | 0.008 | 1.175 | 0.13333 |  |  |  | 7 |  | -0.02 | 0.6673 | 0.085714 | 0.14689 | 0.03 | 0.24287 |  | 0.06 | 0.4

## SA
GENERAL INPUTS
Display name of asset | Monash TS | Mt Barker S TS | Hummocks TS | Clare ZS
Short name of asset | Riverlands | Mount Barker South | Hummocks | Clare 33/11kV
Full name of asset | Riverlands (Monash BSP) | Mount Barker South BSP | Hummocks ZS | Clare 33/11kV ZS
Region | SA | SA | SA | SA
Asset type | TS | TS | TS | TS
Provider | Electranet | Electranet | Electranet | Electranet
Associated Tx
Associated STL
Latitude | -34.2377 | -35.0848 | -33.7853 | -33.8332
Longitude | 140.597 | 138.8486 | 138.2035 | 138.6106
POE value | 0.1 | 0.1 | 0.1 | 0.1
Season to use |  |  |  | Summer
Land available | TRUE | TRUE | TRUE | TRUE
Notes for outputsheet | If in sufficient network capability is available in Victoria, reinforcement is required. Options range from incremental uprating of 132 kV network (~$10M) to replacement double circuit 275 kV (~$226M). Preferred option would be determined by Regulatory Investment Test for Transmission (RIT-T). | New 275/66kV transformer due to peak load growth | 15 Mvar 132 KV capacitor banks due to voltage drop from peak load growth. Load that impacts this constraint spread between four TS, Hummocks, Kadina East, Ardrosan West, and Dalrymple. | Substation constrained if 10% PoE forecast exceeds N rating or if 3.8MVA load at risk for 50% POE forecast during a contingent event.
Maximum connection | 241 | 374 | 150 | 10
NETWORK INVESTMENT
Proposed investment ($m) | 226 | 11 | 4.5 | 5
Proposed investment year | 2022 | 2023 | 2021 | 2016
Annual Deferral Value of system in 2014 ($/kVA/yr) | 2690.3095 | 103.993 | 84.5088 | 1143.6053
Type of constraint | Growth, None | Growth, None | None, Voltage | Growth, None
Constraint season | Summer | NONE | Summer | Summer
Capacity Shortfall: INVEST YEAR (MVA) | 20.0713 | - | - | 0.34
Capacity Shortfall: Year 10 (MVA) | 49.8426 | 42.1776 | 28.5893 | 3.24
SYSTEM INVESTMENT
Investment for system ($m) | 226 | 11 | 4.5 | 5
Investment for ZS ($m)
Investment for Stli ($m)
Investment for TS ($m) | 226 | 11 | 4.5 | 5
Investment year for system | 2022 | 2023 | 2021 | 2016
Investment year for ZS
Investment year for Stli
Investment year for TS | 2022 | 2023 | 2021 | 2016
System capacity shortfall: INVEST YEAR (MVA) | 20.0713 | - | - | 0.34
ZS capacity shortfall: INVEST YEAR (MVA)
Stli capacity shortfall: INVEST YEAR (MVA)
TS capacity shortfall: INVEST YEAR (MVA) | 20.0713 | - | - | 0.34
System capacity shortfall: Year 10 (MVA) | 49.8426 | 42.1776 | 28.5893 | 3.24
ZS capacity shortfall: Year 10 (MVA)
Stli capacity shortfall: Year 10 (MVA)
TS capacity shortfall: Year 10 (MVA) | 49.8426 | 42.1776 | 28.5893 | 3.24
NET PRESENT VALUE IN 2014 ($m)
of system | 228.0896 | 11.3548 | 4.4308 | 4.1657
of asset | 228.0896 | 11.3548 | 4.4308 | 4.1657
of linked ZS
of linked Stli
of linked TS | 228.0896 | 11.3548 | 4.4308 | 4.1657
AVAILABLE CAPACITY (MVA)
2010 | 0.5 | 62.2 | 24.3 | 0.56
2011 | 2.5 | 52.5 | 27.1 | 2.36
2012 | 9.7 | 69 | 29.8 | 1.16
2013 | 0.8 | 62 | 29.3 | 0.36
2014 | -7.7103 | 55.61 | 21.441 | 0.16
2015 | -9.0043 | 51.9733 | 20.5709 | -0.04
2016 | -10.5191 | 48.1389 | 17.8516 | -0.34
2017 | -12.065 | 43.3872 | 15.0379 | -0.54
2018 | -13.6223 | 38.418 | 12.0749 | -0.74
2019 | -15.2013 | 33.2108 | 8.977 | -1.04
2020 | -16.8023 | 27.7646 | 5.7386 | -1.24
2021 | -18.4255 | 22.0478 | 2.3739 | -1.54
2022 | -20.0713 | 16.0583 | -1.1632 | -1.74
ANNUAL DEFERRAL VALUES or ADV
ADV OF Asset ($/kVA/year)
2010 | 2052.4242 | 79.3358 | 64.4714 | 872.451
2011 | 2196.0939 | 84.8893 | 68.9844 | 933.5226
2012 | 2349.8205 | 90.8315 | 73.8133 | 998.8692
2013 | 2514.308 | 97.1897 | 78.9802 | 1068.79
2014 | 2690.3095 | 103.993 | 84.5088 | 1143.6053
2015 | 2878.6312 | 111.2725 | 90.4244 | 1223.6577
2016 | 3080.1354 | 119.0616 | 96.7541 | 1309.3137
2017 | 3295.7448 | 127.3959 | 103.5269 | -
2018 | 9586.6048 | 127.754 | 100.9341 | -
2019 | 10257.6671 | 136.6968 | 107.9995 | -
2020 | 10975.7038 | 146.2655 | 115.5595 | -
2021 | 11744.0031 | 156.5041 | 123.6486 | -
2022 | 12566.0833 | 167.4594 | - | -
ADV OF LINKED Stli ($/kVA/year)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
ADV OF LINKED TS ($/kVA/year)
2010 | 2052.4242 | 79.3358 | 64.4714 | 872.451
2011 | 2196.0939 | 84.8893 | 68.9844 | 933.5226
2012 | 2349.8205 | 90.8315 | 73.8133 | 998.8692
2013 | 2514.308 | 97.1897 | 78.9802 | 1068.79
2014 | 2690.3095 | 103.993 | 84.5088 | 1143.6053
2015 | 2878.6312 | 111.2725 | 90.4244 | 1223.6577
2016 | 3080.1354 | 119.0616 | 96.7541 | 1309.3137
2017 | 3295.7448 | 127.3959 | 103.5269 | -
2018 | 9586.6048 | 127.754 | 100.9341 | -
2019 | 10257.6671 | 136.6968 | 107.9995 | -
2020 | 10975.7038 | 146.2655 | 115.5595 | -
2021 | 11744.0031 | 156.5041 | 123.6486 | -
2022 | 12566.0833 | 167.4594 | - | -
ADV OF SYSTEM ($/kVA/year)
2010 | 2052.4242 | 79.3358 | 64.4714 | 872.451
2011 | 2196.0939 | 84.8893 | 68.9844 | 933.5226
2012 | 2349.8205 | 90.8315 | 73.8133 | 998.8692
2013 | 2514.308 | 97.1897 | 78.9802 | 1068.79
2014 | 2690.3095 | 103.993 | 84.5088 | 1143.6053
2015 | 2878.6312 | 111.2725 | 90.4244 | 1223.6577
2016 | 3080.1354 | 119.0616 | 96.7541 | 1309.3137
2017 | 3295.7448 | 127.3959 | 103.5269 | -
2018 | 9586.6048 | 127.754 | 100.9341 | -
2019 | 10257.6671 | 136.6968 | 107.9995 | -
2020 | 10975.7038 | 146.2655 | 115.5595 | -
2021 | 11744.0031 | 156.5041 | 123.6486 | -
2022 | 12566.0833 | 167.4594 | - | -
HOURLY EXCEEDANCES: INVEST YEAR
Investment trigger point (MVA) | 110 | 149 | 85 | 11.16
Year | 2022 | 2023 | 2021 | 2016
No. of hours over the trigger point (hr) | 44 | - | -
Duration of Exceedance by Month INVEST YEAR (total number of hours on worst day) (hr)
January | 13 | - | -
February | 10 | - | -
March | - | - | -
April | - | - | -
May | - | - | -
June | - | - | -
July | - | - | -
August | - | - | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 7 | - | -
Duration of Exceedance by Month INVEST YEAR (number of consecuative hours on worst day) (hr)
January | 13 | - | -
February | 10 | - | -
March | - | - | -
April | - | - | -
May | - | - | -
June | - | - | -
July | - | - | -
August | - | - | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 7 | - | -
MAX EXCEEDANCE BY MONTH: INVEST YEAR (MVA)
January | 20.0713 | - | -
February | 17.527 | - | -
March | - | - | -
April | - | - | -
May | - | - | -
June | - | - | -
July | - | - | -
August | - | - | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 8.1718 | - | -
Number of days of Exceedance by Month: INVEST YEAR (days)
January | 2 | - | -
February | 2 | - | -
March | - | - | -
April | - | - | -
May | - | - | -
June | - | - | -
July | - | - | -
August | - | - | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 1 | - | -
HOURLY EXCEEDANCES: Year 10
Investment trigger point (MVA) | 110 | 149 | 85 | 11.16
Year | 2032 | 2033 | 2031 | 2026
No. of hours over the trigger point (hr) | 185 | 34 | 57
Duration of Exceedance by Month Year 10 (total number of hours on worst day) (hr)
January | 17 | 9 | 12
February | 20 | - | 4
March | - | - | -
April | - | - | -
May | - | - | -
June | - | 3 | -
July | - | 1 | -
August | - | 1 | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 17 | - | 10
Duration of Exceedance by Month Year 10 (number of consecuative hours on worst day) (hr)
January | 17 | 9 | 12
February | 17 | - | 4
March | - | - | -
April | - | - | -
May | - | - | -
June | - | 2 | -
July | - | 1 | -
August | - | 1 | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 15 | - | 10
MAX EXCEEDANCE BY MONTH: Year 10 (MVA)
January | 49.8426 | 42.1776 | 28.5893
February | 46.716 | - | 6.8684
March | - | - | -
April | - | - | -
May | - | - | -
June | - | 6.4233 | -
July | - | 0.15759 | -
August | - | 0.25588 | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 35.2195 | - | 20.9622
Number of days of Exceedance by Month: Year 10 (days)
January | 11 | 2 | 5
February | 7 | - | 3
March | - | - | -
April | - | - | -
May | - | - | -
June | - | 14 | -
July | - | 1 | -
August | - | 1 | -
September | - | - | -
October | - | - | -
November | - | - | -
December | 3 | - | 2
LOAD PROFILE: INVEST YEAR (MVA)
Year | 2022 | 2023 | 2021 | 2016
Peak load (MVA) | 130.0713 | 138.2359 | 82.6261 | 11.5
Investment trigger point (MVA) | 110 | 149 | 85 | 11.16
PEAK DAY LOAD PROFILE: INVEST YEAR (MVA)
12 am | 86.7821 | 82.1831 | 46.0547
1 am | 81.1733 | 65.1433 | 39.6155
2 am | 76.4126 | 54.2391 | 35.2162
3 am | 73.5017 | 50.5115 | 33.844
4 am | 72.0677 | 49.9411 | 33.5665
5 am | 72.5689 | 52.4647 | 34.7483
6 am | 80.9084 | 65.9339 | 39.0546
7 am | 91.0277 | 80.1696 | 48.687
8 am | 96.4636 | 83.3252 | 57.9782
9 am | 103.4503 | 91.8433 | 66.106
10 am | 110.4913 | 99.638 | 70.5789
11 am | 116.8148 | 106.9514 | 76.1573
12 pm | 122.2302 | 112.3748 | 77.9043
1 pm | 126.5344 | 120.9217 | 80.3435
2 pm | 128.8267 | 124.8996 | 81.4124
3 pm | 129.4903 | 127.6752 | 82.6261
4 pm | 130.0713 | 133.7321 | 81.9243
5 pm | 129.5607 | 138.2359 | 80.9245
6 pm | 128.918 | 138.1816 | 79.1848
7 pm | 129.3627 | 130.4411 | 75.1336
8 pm | 126.0257 | 119.6079 | 69.4529
9 pm | 121.3988 | 105.094 | 61.708
10 pm | 112.1813 | 84.0226 | 51.4949
11 pm | 104.7136 | 72.7265 | 46.313
LOAD PROFILE: Year 10 (MVA)
Year | 2032 | 2033 | 2031 | 2026
Peak load (MVA) | 159.8426 | 191.1776 | 113.5893 | 14.4
Investment trigger point (MVA) | 110 | 149 | 85 | 11.16
PEAK DAY LOAD PROFILE: Year 10 (MVA)
12 am | 106.6452 | 113.6576 | 63.3132
1 am | 99.7526 | 90.092 | 54.4609
2 am | 93.9023 | 75.0116 | 48.4131
3 am | 90.3251 | 69.8565 | 46.5267
4 am | 88.5628 | 69.0676 | 46.1452
5 am | 89.1788 | 72.5577 | 47.7699
6 am | 99.4271 | 91.1853 | 53.6898
7 am | 111.8625 | 110.873 | 66.9319
8 am | 118.5426 | 115.2372 | 79.7049
9 am | 127.1284 | 127.0176 | 90.8785
10 am | 135.781 | 137.7974 | 97.0276
11 am | 143.5519 | 147.9117 | 104.6964
12 pm | 150.2068 | 155.4122 | 107.098
1 pm | 155.4962 | 167.2325 | 110.4513
2 pm | 158.3132 | 172.7338 | 111.9208
3 pm | 159.1286 | 176.5723 | 113.5893
4 pm | 159.8426 | 184.949 | 112.6245
5 pm | 159.2152 | 191.1776 | 111.25
6 pm | 158.4253 | 191.1025 | 108.8584
7 pm | 158.9718 | 180.3975 | 103.2891
8 pm | 154.871 | 165.4155 | 95.4796
9 pm | 149.185 | 145.343 | 84.8324
10 pm | 137.8578 | 116.2017 | 70.7921
11 pm | 128.6809 | 100.5793 | 63.6683
SUMMER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 241 | 374 | 150 | 10
n-1 capacity (MVA) | 110 | 149 | 85 | 10
Secure capacity (MVA) | 110 | 149 | 85 | 10
Reliability requirement | N-1 | N-1 | N-1 | N
Actual/forecast peak load: Summer (MVA)
2010 | 109.5 | 86.8 | 60.7 | 10.6
2011 | 107.5 | 96.5 | 57.9 | 8.8
2012 | 100.3 | 80 | 55.2 | 10
2013 | 109.2 | 87 | 55.7 | 10.8
2014 | 117.7103 | 93.39 | 63.559 | 11
2015 | 119.0043 | 97.0267 | 64.4291 | 11.2
2016 | 120.5191 | 100.8611 | 67.1484 | 11.5
2017 | 122.065 | 105.6128 | 69.9621 | 11.7
2018 | 123.6223 | 110.582 | 72.9251 | 11.9
2019 | 125.2013 | 115.7892 | 76.023 | 12.2
2020 | 126.8023 | 121.2354 | 79.2614 | 12.4
2021 | 128.4255 | 126.9522 | 82.6261 | 12.7
2022 | 130.0713 | 132.9417 | 86.1632 | 12.9
Average Growth (MVA/yr)
2012 to 2017 | 4.353 | 5.1226 | 2.9524 | 0.34
2017 to 2022 | 1.6013 | 5.4658 | 3.2402 | 0.24
2022 onwards | 2.9771 | 5.2942 | 3.0473 | 0.375
WINTER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 241 | 374 | 150 | 10
n-1 capacity (MVA) | 110 | 149 | 85 | 10
Secure capacity (MVA) | 110 | 149 | 85 | 10
Reliability requirement
Actual/forecast peak load: Winter (MVA)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
Average Growth (MVA/yr)
2012 to 2017
2017 to 2022
2022 onwards

## Qld
GENERAL INPUTS
Display name of asset | Warwick BSP | Stanthorpe ZS | Roma BSP | Lilyvale TS | Millchester BSP | Chinchilla BSP | Dysart BSP | Moonstone ZS | Roma ZS | Clifton ZS | West Warwick ZS | Pampas ZS | Stanthorpe Town ZS | Clermont ZS | Yarranlea ZS | Warwick ZS | West Dalby ZS | Torrington ZS | Cape River ZS | Chinchilla Town ZS | Roma E ZS | Roma W ZS | Charleville ZS | Emerald ZS | Millchester ZS | St George ZS | Blackwater ZS | Dysart ZS
Short name of asset | 60025700 | 60025701 | 60025702 | 40000022 | 20010917 | 60025697 | 40000020 | Proposed Moonstone 132/22kV (Alpha) ZS | 60025702_ZS | 60007249 | 60007247 | 60007229 | 60007222 | 40000023_ZS | 60025696_ZS | 60025700_ZS | 60007197 | 60025703 | 20003948 | 60025697_ZS | 60007250 | 60007251 | 60007255 | 40017951 | 20010917_ZS | 60007215 | 40000019 | 40000020_ZS
Full name of asset | T058 Warwick | Stanthorpe 110/33kV ZS | T083 Roma BSS | Lilyvale 132/66kV TS | Millchester 132/66kV BSP | T013 Chinchilla CHIN | Dysart 132/66/22kV BSP | Proposed Moonstone 132/22kV (Alpha) ZS | ROMA ZS | Clifton 33/11kV ZS | West Warwick 33/11kV ZS | Pampas 33/11kV ZS | Stanthorpe Town 33/11kV ZS | Clermont 132/22kV ZS | Yarranlea 110/33kV ZS | Warwick 110/33kV ZS | West Dalby 33/11kV ZS | Torrington 33/11kV ZS | Cape River 66/11 kV ZS | Chinchilla Town ZS | Roma East 33/11kV ZS | Roma West 33/11kV ZS | Charleville 66/22/11 ZS | Emerald 66/22kV ZS | Millchester 66/11kV ZS | St George 66/33kV ZS | Blackwater 132/11/22kV ZS | Dysart ZS
Region | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld | Qld
Asset type | TS | TS | TS | TS | TS | TS | TS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS | ZS
Provider | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon | Ergon
Associated Tx |  | 60025700 | [6 empty] | 60025702 | 60025700 | 60025700 |  | 60025701 | 40000023 |  | 60025700 |  |  | 20010917 | 60025697 | 60025702 | 60025702 |  |  | 20010917 |  |  | 40000020
Associated STL | [20 empty] | Roma North Feeder | Roma North Feeder
Latitude | -28.1969 | -28.6454 | -26.5781 | -23.1304 | -20.1009 | -26.7446 | -22.5476 | -23.6484 | -26.5781 | -27.9366 | -28.2158 | -27.7519 | -28.6489 | -22.8491 | -27.7219 | -28.1969 | -27.1796 | -27.5564 | -20.4761 | -26.7446 | -26.5747 | -26.571 | -26.4062 | -23.5362 | -20.1009 | -28.0556 | -23.5872 | -22.5476
Longitude | 152.0508 | 151.917 | 148.8399 | 148.4265 | 146.2805 | 150.6454 | 148.4055 | 146.6406 | 148.8399 | 151.9379 | 152.0012 | 151.3508 | 151.9375 | 147.6109 | 151.5309 | 152.0508 | 151.2554 | 151.8996 | 145.4659 | 150.6454 | 148.7988 | 148.7708 | 146.2838 | 148.1515 | 146.2805 | 148.6287 | 148.8251 | 148.4055
POE value | 50 | 50 | 50 | 50 | 50 | 10 | 50 | Unknown | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Season to use
Land available | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Notes for outputsheet | Re-build Middle Ridge-Warwick 110kV Feeder 735 as new 132kV SC Oxygen line. To provide N-1 110kV fdr capacity to Warwick & Stanthorpe. | Establish new additional Warwick-Stanthorpe 110kV line (63km) and a suite of other measures to meet n-1 SOS criteria at BSP. | To allow adequate volts at Roma in 132kV line contingency, as currently may breach Security Criteria. To address feeder capacity issue in short term, network support agreement has been put in place for Roma Power Station to support the volts in the event of 132kV feeder contingency. In longer term, either: i) Evaluate non-network solutions . ii) install SVC at Roma sub by November 2022. | Upgrade 66kV switchyard to cater for Powerlink TF upgrade. Linked to works at Dysart BBS/ZS. | Establish 2nd single circuit 132kV line to Millchester sub including 132kV switchworks at Milchester sub to provide N-1 capacity to Millchester BSP. 2nd project to replace 34MVA 132/66kV TF at Milchester sub with 63MVA unit. Required to maintain N-1 TF capacity. Millchester 132/66kV BSP supplied by single 132kV line from Ross sub, with partial backup via 66kV line from Clare South & Stuart. Project will install a 2nd 132kV line to Millchester sub, with Ross being the preferred source. | Replace 110/33kV TF/Reg combinations with 132/33kV TF. Use ex-Roma 40MVA 132/33kV TF. TS classified as C&I & requires full N-1 TF capacity when MD is >5MVA ($2.5M in 2019). | Install 66kV TF bay connecting Powerlinks 100MVA 3rd 132/66kV TF to Dysart ZS. Required to connect Powerlinks proposed 100MVA 3rd 132/66kV TF to the 66kV network ($1.5m in Sep 2015). Dysart 66/22kV TFs - Install 2 x 20MVA 66/22kV TFs & disconnect Powerlink QLD tertiary windings from distribution network. Carry out 66kV switchyard augmentation works associated with larger TF. Powerlink QLD replacing No1 TF with 100MVA unit & removing No2 TF. They will not allow connection of tertiary windings of new TFs to supply the Ergon distribution network. The new larger BS TF & increased 66kV demand may require augmentation to 66kV switchyard ($7.5m in Oct 2016). | Establish new ZS due to expected significant demand growth from mining activities. Exisitng network has very limited capacity & presently usesi diesel generator to supply peak loads. For the shorter term, further refinement of the generator solution has been undertaken (including better control & monitoring via SCADA). In the longer term, a better solution may be to establish a 132/22kV ZS near the existing 132kV line from Clermont to Barcaldine and establish 22kV feeders out of this new ZS to supply the Alpha area. | NOTE: POE forecast is the addition of ROMA (T083) 132/33kV ROMA and ROMA (T083) 132/66kV ROMA | If/when capacity, security & low voltage issues occur on subtransmission network supplying Allora, Clifton & Mt Sibley substations, the proposed longer term solution is to establish a new Clifton East 110/33kV BSP. This sub will be located east of Clifton, adjacent to the Middle Ridge-Warwick feeder 736 110kV line. This sub is to be supplied by cutting it into Feeder 736. | Install new 33kV line from East Warwick ZS to West Warwick ZS to allow connection of new feeder, and new 33kv fdr bay at T58 Warwick, to provide N-1 capacity to West Warwick ZS. | Replace 33/11kV Pampas ZS with new 2 x 15MVA 66/11kV ZS (2 x T3-15). To include 66/33kV step down TF to supply 33kV feeder to Millmerran. Reason for work is Pampus is heavily loaded & aged. It is to be converted to a 66kV, in line with sub-transmission conversion plan. | Install 33kV & 11kV TF Circuit Breakers & additional 33kV incomer feeder bay, Increase clearances on the Pozieres 33kV line between T60 & ME2 to allow operation at 75oC. Linked to Stanthorpe requirements for n-1. | Install 20MVA 66/22kV TF at Clermont ZS & AFLC injector connected to the 66kV bus. Required as load exceeds 15MVA & N-1 capacity of the present tertiary winding supply arrangement ($4.8m in 2023). | Works for proposed new Victoria Hills ZS attributed to Yarranlea ZS. The timing is uncertain at this stage. |  | Install 33kV TF & feeder CBs at West Dalby ZS. This will allow T02 Dalby East to supply Central and West Dalby ZS in 33kV closed ring arrangement & provide full N-1 33kV feeder capacity to both ZS (with full N-1 TF capacity provided by load transfer & installation of 33kV TF CB). | North St BSP link to Postmans Ridge for ~$40m in 2021 | Load west of Cape River has reached firm capacity of the 66kV regulators. Project to establish bypass & feeder tie arrangement to allow more operational flexibility, & shorter restoration times, for regulator or 66kV line outage. Work to be completed in conjunction with proposed SCADA & protection upgrade projects for Cape River ZS. Once the 66kV demand exceeds 15MVA for loads west of Cape River, security increases to N-1(b) SOS criteria. | 33/11kV ZS & CHIN-SKID Chinchilla 33/11kV Skid Mount ZS referred to as Chinchilla (T013) 33/11kV in latest POE forecast. Chinchilla Town 33/11kV ZS has MD of >5MVA & is classified as Sig C & I sub. Therefore, requires full N-1 transformer & 33kV feeder capacity under the Security of Supply criteria. To restore compliance, proposal to establish 11kV injection point at T13 Chinchilla BSP in 2017 & de-load Chinchilla Town ZS to <5MVA. Investment attributed at Chinchilla Town ZS, as load growth has invoked investment at BSP. | Roma East and Roma West 33/11kV ZS classified as Sig C & I ZS, & have MDs of >5MVA but netiher complies N-1 Security of Supply criteria. Project to rebuild aged & poor condition of Roma West 2 x 2.5MVA sub into a 2 x 10MVA in 2014. A suite of projects are included to remove overloads and restore compliance with the criteria. | Roma East and Roma West 33/11kV ZS classified as Sig C & I ZS, & have MDs of >5MVA but netiher complies N-1 Security of Supply criteria. Project to rebuild aged & poor condition of Roma West 2 x 2.5MVA sub into a 2 x 10MVA in 2014. A suite of projects are included to remove overloads and restore compliance with the criteria. | Expected network augmentation costs ~$70m for N-1 solution for 50 year period if a demand reduction opportunity is not found to keep load <15 MVA. | To provide support to distribution network & de-load existing Emerald ZS, supplied by 2 long 66kV feeders. 2 projects to ensure adequate network capacity for forecast growth: rebuild existing aged Blackwater-Emerald 66kV line as new double circuit 66kV line by 2015 to provide N-1 66kV feeder capacity, plus establish new Emerald North ZS in 2020 to relieve constrained 22kV distribution network & provide long term capacity to meet future loads. | Investment at bulk supply point | Expected network augmentation costs ~$70m for N-1 solution for a 50 year period at St George, if a demand reduction opportunity is not found to keep load <15 MVA. | (22kV TF Augmentation) - Install 32MVA 66/22kV TF as does not provide N-1 regulator capacity ($4m in 2018). (22kV Regulator & 66kV Switchyard Augmentation) - Perform 66kV upgrade works to cater for Powerlink TF upgrade & replace 10MVA 11/22kV regulator with 32MVA unit ($3.85m in 2020).
Maximum connection | 111 | 75.8 | 176 | 264 | 74.8 | 30 | 140 |  | 176 | 7.8 | 27.7 | 11 | 15.2 | 20 | 30 | 111 | 15 | 55 | 20 | 15.5 | 15 | 5 | 20 | 69.8 | 15 | 44 | 22 | 20
NETWORK INVESTMENT
Proposed investment ($m) | 35 | 80 | 14 | 2.5 | 46 | 2.5 | 9 | 15 |  | 1 | 4.75 | 17 | 4.5 | 4.8 | 10 |  | 2.6 | 40 | 5.5 | 5.5 | 5.05 | 0.9 | 70 | 24 |  | 70 | 7.85
Proposed investment year | 2017 | 2017 | 2022 | 2017 | 2017 | 2019 | 2015 | 2017 |  | 2022 | 2016 | 2019 | 2017 | 2023 | 2024 |  | 2016 | 2021 | 2022 | 2017 | 2015 | 2014 | 2022 | 2020 |  | 2022 | 2018
Annual Deferral Value of system in 2014 ($/kVA/yr) | 165.1766 | - | 323.8638 | 69.349 | 167.1588 | 24.7967 | 143.4633 |  | 323.8638 | 2756.0872 | 165.1766 | 10791.5212 | - | - | - | 165.1766 | - | 2217.8194 | 167.1588 | 24.7967 | 323.8638 | 323.8638 | - | 71.192 | 167.1588 | 483.6366 | 5331.9636 | 143.4633
Type of constraint | N-1 Security of Supply | N-1 Security of Supply | Voltage | Growth, None | N-1 Security of Supply | N-1 Security of Supply | Growth, None |  | None | Voltage | N-1 Security of Supply | Growth, None | N-1 Security of Supply | N-1 Security of Supply | Growth | None | N-1 Security of Supply | Growth | N-1 Security of Supply | N-1 Security of Supply | N-1 Security of Supply | N-1 Security of Supply | N-1 Security of Supply | N-1 Security of Supply | None | N-1 Security of Supply | N-1 Security of Supply | None
Constraint season | BOTH | NONE | BOTH (Summer) | Summer | BOTH | BOTH | BOTH |  |  | Winter | NONE | Summer | NONE | NONE | Summer |  | NONE | BOTH (Winter) | NONE | NONE | Summer | NONE | NONE | BOTH |  | Winter | NONE
Capacity Shortfall: INVEST YEAR (MVA) | 20 | 20 | 2.23 | 2.98 | 20 | 20 | - |  | - | 0.06 | 20 | 0.14 | 15 | 20 | 0.2 | - | 15 | 1.8 | 20 | 15 | 15 | 20 | 20 | 20 |  | 20 | 20 | -
Capacity Shortfall: Year 10 (MVA) | 26.5 | 20 | 24.53 | 30.98 | 26.2 | 20 | 33.8 |  | - | 0.66 | 20 | 1.34 | 15 | 20 | 2.2 | - | 15 | 15.8 | 20 | 15.5 | 17.1 | 20 | 20 | 33.9 |  | 26.6 | 21.2 | -
SYSTEM INVESTMENT
Investment for system ($m) | 35 | 80 | 14 | 2.5 | 46 | 2.5 | 9 | 15 | 14 | 36 | 39.75 | 17 | 84.5 | 4.8 | 10 | 35 | 2.6 | 40 | 51.5 | 8 | 19.05 | 14.9 | 70 | 24 | 46 | 70 | 7.85 | 9
Investment for ZS ($m) | [7 empty] | 15 |  | 1 | 4.75 | 17 | 4.5 | 4.8 | 10 |  | 2.6 | 40 | 5.5 | 5.5 | 5.05 | 0.9 | 70 | 24 |  | 70 | 7.85
Investment for Stli ($m)
Investment for TS ($m) | 35 | 80 | 14 | 2.5 | 46 | 2.5 | 9 |  | 14 | 35 | 35 |  | 80 |  |  | 35 |  |  | 46 | 2.5 | 14 | 14 |  |  | 46 |  |  | 9
Investment year for system | 2017 | 2017 | 2022 | 2017 | 2017 | 2019 | 2015 | 2017 | 2022 | 2017 | 2016 | 2019 | 2017 | 2023 | 2024 | 2017 | 2016 | 2021 | 2017 | 2017 | 2015 | 2014 | 2022 | 2020 | 2017 | 2022 | 2018 | 2015
Investment year for ZS | [7 empty] | 2017 |  | 2022 | 2016 | 2019 | 2017 | 2023 | 2024 |  | 2016 | 2021 | 2022 | 2017 | 2015 | 2014 | 2022 | 2020 |  | 2022 | 2018
Investment year for Stli
Investment year for TS | 2017 | 2017 | 2022 | 2017 | 2017 | 2019 | 2015 |  | 2022 | 2017 | 2017 |  | 2017 |  |  | 2017 |  |  | 2017 | 2019 | 2022 | 2022 |  |  | 2017 |  |  | 2015
System capacity shortfall: INVEST YEAR (MVA) | 20 | 20 | 2.23 | 2.98 | 20 | 20 | - |  | 2.23 | 20 | 20 | 0.14 | 20 | 20 | 0.2 | 20 | 15 | 1.8 | 20 | 20 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | -
ZS capacity shortfall: INVEST YEAR (MVA) | [8 empty] | - | 0.06 | 20 | 0.14 | 15 | 20 | 0.2 | - | 15 | 1.8 | 20 | 15 | 15 | 20 | 20 | 20 |  | 20 | 20 | -
Stli capacity shortfall: INVEST YEAR (MVA)
TS capacity shortfall: INVEST YEAR (MVA) | 20 | 20 | 2.23 | 2.98 | 20 | 20 | - |  | 2.23 | 20 | 20 |  | 20 |  |  | 20 |  |  | 20 | 20 | 2.23 | 2.23 |  |  | 20 |  |  | -
System capacity shortfall: Year 10 (MVA) | 26.5 | 20 | 24.53 | 30.98 | 26.2 | 20 | 33.8 |  | 24.53 | 26.5 | 26.5 | 1.34 | 20 | 20 | 2.2 | 26.5 | 15 | 15.8 | 26.2 | 20 | 24.53 | 24.53 | 20 | 33.9 | 26.2 | 26.6 | 21.2 | 33.8
ZS capacity shortfall: Year 10 (MVA) | [8 empty] | - | 0.66 | 20 | 1.34 | 15 | 20 | 2.2 | - | 15 | 15.8 | 20 | 15.5 | 17.1 | 20 | 20 | 33.9 |  | 26.6 | 21.2 | -
Stli capacity shortfall: Year 10 (MVA)
TS capacity shortfall: Year 10 (MVA) | 26.5 | 20 | 24.53 | 30.98 | 26.2 | 20 | 33.8 |  | 24.53 | 26.5 | 26.5 |  | 20 |  |  | 26.5 |  |  | 26.2 | 20 | 24.53 | 24.53 |  |  | 26.2 |  |  | 33.8
NET PRESENT VALUE IN 2014 ($m)
of system | 30.3685 | 69.4137 | 14.1294 | 2.1692 | 39.9129 | 2.3252 | 7.1658 | 13.0151 | 14.1294 | 31.3777 | 34.3259 | 15.8117 | 73.3182 | 4.9548 | 10.5376 | 30.3685 | 2.1662 | 39.3851 | 45.4637 | 7.0974 | 18.1502 | 14.8104 | 70.6472 | 22.9989 | 39.9129 | 70.6472 | 7.0645 | 7.1658
of asset | 30.3685 | 69.4137 | 14.1294 | 2.1692 | 39.9129 | 2.3252 | 7.1658 | 13.0151 |  | 1.0092 | 3.9574 | 15.8117 | 3.9045 | 4.9548 | 10.5376 |  | 2.1662 | 39.3851 | 5.5509 | 4.7722 | 4.0208 | 0.681 | 70.6472 | 22.9989 |  | 70.6472 | 7.0645
of linked ZS | [7 empty] | 13.0151 |  | 1.0092 | 3.9574 | 15.8117 | 3.9045 | 4.9548 | 10.5376 |  | 2.1662 | 39.3851 | 5.5509 | 4.7722 | 4.0208 | 0.681 | 70.6472 | 22.9989 |  | 70.6472 | 7.0645
of linked Stli
of linked TS | 30.3685 | 69.4137 | 14.1294 | 2.1692 | 39.9129 | 2.3252 | 7.1658 |  | 14.1294 | 30.3685 | 30.3685 |  | 69.4137 |  |  | 30.3685 |  |  | 39.9129 | 2.3252 | 14.1294 | 14.1294 |  |  | 39.9129 |  |  | 7.1658
AVAILABLE CAPACITY (MVA)
2010 | -13.866 | 6.3 | 19.37 | 17.52 | -13.6 | -7.4 | 5.8 |  |  | 0.84 | 8.8 | 1.06 | 3.4 | 10.5 | -0.2 |  | 12.9 | 13.9 | 19 | 7.6 | 7 | 13.2 | 9.9 | -16.6 |  | 8.5 | 9.7
2011 | -9.3 | 6.8 | 10.77 | 23.82 | -12.6 | -6.3 | 7.2 |  |  | 0.84 | 7.9 | 3.56 | 4 | 11.2 | 4.3 |  | 5.6 | 12.3 | 19 | 7.2 | 6.2 | 14.2 | 9.7 | -16.1 |  | 5.1 | 10.2
2012 | -8.9 | 6 | 20.07 | 10.12 | -12.9 | -7.5 | 2.1 |  |  | 0.54 | 6.6 | 0.46 | 2.5 | 9.1 | 2.2 |  | 7.3 | 10.6 | 19.4 | 5 | 7.1 | 14.6 | 9.3 | -19 |  | 4.1 | 8.1
2013 | -8.8 | 5.9 | 14.97 | 7.22 | -16.1 | 0.4 | -1.5 |  |  | 0.54 | 6 | -0.14 | 2.4 | 8.7 | 2.5 |  | 5.7 | 9.4 | 19.4 | 4.1 | 4.8 | 13.4 | 9 | -22.1 |  | 1.3 | 7.4
2014 | -8.3 | 6.3 | 13.87 | 0.72 | -15.3 | 0.6 | 0.5 |  |  | 0.64 | 7.9 | 0.16 | 2.8 | 8.9 | 3.2 |  | 11.5 | 9.3 | 19.4 | 4.3 | 4.8 | 13.4 | 9.1 | -21.4 |  | 1.7 | 6.9
2015 | -9 | 6.3 | 12.27 | 0.12 | -15.6 | 0.1 | 0.3 |  |  | 0.54 | 7.5 | 0.06 | 2.8 | 8.5 | 3 |  | 11.4 | 8.2 | 19.4 | 4 | 4.3 | 13.1 | 8.7 | -22.5 |  | 1.4 | 6.3
2016 | -9.3 | 6.2 | 11.27 | 0.72 | -15.5 | 0.4 | -5.9 |  |  | 0.54 | 7 | 0.06 | 2.8 | 8.3 | 2.9 |  | 11.3 | 7.2 | 19.4 | 3.8 | 4 | 12.9 | 8.5 | -23.3 |  | 1.2 | 6
2017 | -10.4 | 6 | 8.87 | -2.98 | -16.3 | -0.6 | -24 |  |  | 0.44 | 6.4 | -0.04 | 2.7 | 7.8 | 2.4 |  | 11.2 | 5.6 | 19.4 | 3.3 | 3.4 | 12.5 | 8 | -25 |  | 0.6 | 5.3
2018 | -10.7 | 5.9 | 8.17 | -2.88 | -16.1 | -1 | -24.7 |  |  | 0.44 | 5.8 | -0.04 | 2.6 | 7.6 | 2.4 |  | 11.1 | 4.3 | 19.4 | 3.2 | 3.1 | 12.3 | 7.6 | -25.6 |  | 0.2 | 4.9
2019 | -11.7 | 5.6 | 5.87 | -5.98 | -16.7 | -1.4 | -26.2 |  |  | 0.34 | 5.1 | -0.14 | 2.4 | 7.2 | 2 |  | 11 | 2.6 | 19.4 | 2.8 | 2.6 | 11.9 | 7.2 | -27.1 |  | -0.3 | 4.3
2020 | -13.4 | 5 | 2.07 | -12.48 | -18.1 | -2.7 | -29.9 |  |  | 0.14 | 4 | -0.54 | 1.9 | 6.4 | 1 |  | 10.8 | -0.1 | 19.3 | 2 | 1.7 | 11.3 | 6.3 | -29.9 |  | -1.5 | 3.3
2021 | -14.4 | 4.7 | -0.03 | -15.18 | -18.6 | -3.1 | -31.3 |  |  | 0.04 | 3.3 | -0.64 | 1.8 | 6 | 0.6 |  | 10.6 | -1.8 | 19.3 | 1.7 | 1.2 | 11 | 5.8 | -31.4 |  | -2 | 2.7
2022 | -15.4 | 4.6 | -2.23 | -17.88 | -19.1 | -3.7 | -32 |  |  | -0.06 | 2.6 | -0.74 | 1.7 | 5.6 | 0.2 |  | 10.5 | -3.4 | 19.3 | 1.2 | 0.7 | 10.6 | 5.4 | -32.9 |  | -2.5 | 2
ANNUAL DEFERRAL VALUES or ADV
ADV OF Asset ($/kVA/year)
2010 | 126.0125 | - | 247.0742 | 52.906 | 127.5246 | 18.9173 | 109.4475 |  |  | 1976.5932 | - | 8232.7998 | - | - | - |  | - | 1691.9638 | - | - | - | - | - | 54.312 |  | 368.9641 | 4067.7295
2011 | 134.8333 | - | 264.3693 | 56.6094 | 136.4513 | 20.2415 | 117.1088 |  |  | 2114.9548 | - | 8809.0958 | - | - | - |  | - | 1810.4013 | - | - | - | - | - | 58.1139 |  | 394.7916 | 4352.4706
2012 | 144.2717 | - | 282.8752 | 60.5721 | 146.0029 | 21.6584 | 125.3064 |  |  | 2263.0016 | - | 9425.7325 | - | - | - |  | - | 1937.1294 | - | - | - | - | - | 62.1819 |  | 422.427 | 4657.1435
2013 | 154.3707 | - | 302.6765 | 64.8121 | 156.2231 | 23.1745 | 134.0779 |  |  | 2421.4117 | - | 10085.5338 | - | - | - |  | - | 2072.7284 | - | - | - | - | - | 66.5346 |  | 451.9969 | 4983.1436
2014 | 165.1766 | - | 323.8638 | 69.349 | 167.1588 | 24.7967 | 143.4633 |  |  | 2590.9105 | - | 10791.5212 | - | - | - |  | - | 2217.8194 | - | - | - | - | - | 71.192 |  | 483.6366 | 5331.9636
2015 | 176.739 | - | 346.5343 | 74.2034 | 178.8599 | 26.5325 | 153.5057 |  |  | 2772.2743 | - | 11546.9276 | - | - | - |  | - | 2373.0668 | - | - | - | - | - | 76.1754 |  | 517.4912 | 5705.2011
2016 | 189.1107 | - | 370.7917 | 79.3976 | 191.3801 | 28.3897 | - |  |  | 2966.3335 | - | 12355.2126 | - | - | - |  | - | 2539.1814 | - | - | - | - | - | 81.5077 |  | 553.7156 | 6104.5652
2017 | 202.3485 | - | 396.7471 | 84.9555 | 204.7767 | 30.377 | - |  |  | 3173.9768 | - | 13220.0774 | - | - | - |  | - | 2716.9241 | - | - | - | - | - | 87.2133 |  | 592.4757 | 6531.8847
2018 | - | - | 428.3439 | - | - | 32.5034 | - |  |  | 679.231 | - | 10103.9163 | - | - | 1348.3334 |  | - | 1615.0605 | - | - | - | - | - | 93.3182 |  | 633.949 | 6989.1167
2019 | - | - | 458.328 | - | - | 34.7786 | - |  |  | 726.7772 | - | 10811.1905 | - | - | 1442.7167 |  | - | 1728.1147 | - | - | - | - | - | 99.8505 |  | 678.3254 | -
2020 | - | - | 490.4109 | - | - | - | - |  |  | 777.6516 | - | - | - | - | 1543.7069 |  | - | 1849.0827 | - | - | - | - | - | 106.84 |  | 725.8082 | -
2021 | - | - | 524.7397 | - | - | - | - |  |  | 832.0872 | - | - | - | - | 1651.7664 |  | - | 1978.5185 | - | - | - | - | - | - |  | 776.6147 | -
2022 | - | - | 561.4715 | - | - | - | - |  |  | 890.3333 | - | - | - | - | 1767.39 |  | - | - | - | - | - | - | - | - |  | 830.9778 | -
ADV OF LINKED Stli ($/kVA/year)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
ADV OF LINKED TS ($/kVA/year)
2010 | 126.0125 | - | 247.0742 | 52.906 | 127.5246 | 18.9173 | 109.4475 |  | 247.0742 | 126.0125 | 126.0125 |  | - |  |  | 126.0125 |  |  | 127.5246 | 18.9173 | 247.0742 | 247.0742 |  |  | 127.5246 |  |  | 109.4475
2011 | 134.8333 | - | 264.3693 | 56.6094 | 136.4513 | 20.2415 | 117.1088 |  | 264.3693 | 134.8333 | 134.8333 |  | - |  |  | 134.8333 |  |  | 136.4513 | 20.2415 | 264.3693 | 264.3693 |  |  | 136.4513 |  |  | 117.1088
2012 | 144.2717 | - | 282.8752 | 60.5721 | 146.0029 | 21.6584 | 125.3064 |  | 282.8752 | 144.2717 | 144.2717 |  | - |  |  | 144.2717 |  |  | 146.0029 | 21.6584 | 282.8752 | 282.8752 |  |  | 146.0029 |  |  | 125.3064
2013 | 154.3707 | - | 302.6765 | 64.8121 | 156.2231 | 23.1745 | 134.0779 |  | 302.6765 | 154.3707 | 154.3707 |  | - |  |  | 154.3707 |  |  | 156.2231 | 23.1745 | 302.6765 | 302.6765 |  |  | 156.2231 |  |  | 134.0779
2014 | 165.1766 | - | 323.8638 | 69.349 | 167.1588 | 24.7967 | 143.4633 |  | 323.8638 | 165.1766 | 165.1766 |  | - |  |  | 165.1766 |  |  | 167.1588 | 24.7967 | 323.8638 | 323.8638 |  |  | 167.1588 |  |  | 143.4633
2015 | 176.739 | - | 346.5343 | 74.2034 | 178.8599 | 26.5325 | 153.5057 |  | 346.5343 | 176.739 | 176.739 |  | - |  |  | 176.739 |  |  | 178.8599 | 26.5325 | 346.5343 | 346.5343 |  |  | 178.8599 |  |  | 153.5057
2016 | 189.1107 | - | 370.7917 | 79.3976 | 191.3801 | 28.3897 | - |  | 370.7917 | 189.1107 | 189.1107 |  | - |  |  | 189.1107 |  |  | 191.3801 | 28.3897 | 370.7917 | 370.7917 |  |  | 191.3801 |  |  | -
2017 | 202.3485 | - | 396.7471 | 84.9555 | 204.7767 | 30.377 | - |  | 396.7471 | 202.3485 | 202.3485 |  | - |  |  | 202.3485 |  |  | 204.7767 | 30.377 | 396.7471 | 396.7471 |  |  | 204.7767 |  |  | -
2018 | - | - | 428.3439 | - | - | 32.5034 | - |  | 428.3439 | - | - |  | - |  |  | - |  |  | - | 32.5034 | 428.3439 | 428.3439 |  |  | - |  |  | -
2019 | - | - | 458.328 | - | - | 34.7786 | - |  | 458.328 | - | - |  | - |  |  | - |  |  | - | 34.7786 | 458.328 | 458.328 |  |  | - |  |  | -
2020 | - | - | 490.4109 | - | - | - | - |  | 490.4109 | - | - |  | - |  |  | - |  |  | - | - | 490.4109 | 490.4109 |  |  | - |  |  | -
2021 | - | - | 524.7397 | - | - | - | - |  | 524.7397 | - | - |  | - |  |  | - |  |  | - | - | 524.7397 | 524.7397 |  |  | - |  |  | -
2022 | - | - | 561.4715 | - | - | - | - |  | 561.4715 | - | - |  | - |  |  | - |  |  | - | - | 561.4715 | 561.4715 |  |  | - |  |  | -
ADV OF SYSTEM ($/kVA/year)
2010 | 126.0125 | - | 247.0742 | 52.906 | 127.5246 | 18.9173 | 109.4475 |  | 247.0742 | 2102.6057 | 126.0125 | 8232.7998 | - | - | - | 126.0125 | - | 1691.9638 | 127.5246 | 18.9173 | 247.0742 | 247.0742 | - | 54.312 | 127.5246 | 368.9641 | 4067.7295 | 109.4475
2011 | 134.8333 | - | 264.3693 | 56.6094 | 136.4513 | 20.2415 | 117.1088 |  | 264.3693 | 2249.7881 | 134.8333 | 8809.0958 | - | - | - | 134.8333 | - | 1810.4013 | 136.4513 | 20.2415 | 264.3693 | 264.3693 | - | 58.1139 | 136.4513 | 394.7916 | 4352.4706 | 117.1088
2012 | 144.2717 | - | 282.8752 | 60.5721 | 146.0029 | 21.6584 | 125.3064 |  | 282.8752 | 2407.2733 | 144.2717 | 9425.7325 | - | - | - | 144.2717 | - | 1937.1294 | 146.0029 | 21.6584 | 282.8752 | 282.8752 | - | 62.1819 | 146.0029 | 422.427 | 4657.1435 | 125.3064
2013 | 154.3707 | - | 302.6765 | 64.8121 | 156.2231 | 23.1745 | 134.0779 |  | 302.6765 | 2575.7824 | 154.3707 | 10085.5338 | - | - | - | 154.3707 | - | 2072.7284 | 156.2231 | 23.1745 | 302.6765 | 302.6765 | - | 66.5346 | 156.2231 | 451.9969 | 4983.1436 | 134.0779
2014 | 165.1766 | - | 323.8638 | 69.349 | 167.1588 | 24.7967 | 143.4633 |  | 323.8638 | 2756.0872 | 165.1766 | 10791.5212 | - | - | - | 165.1766 | - | 2217.8194 | 167.1588 | 24.7967 | 323.8638 | 323.8638 | - | 71.192 | 167.1588 | 483.6366 | 5331.9636 | 143.4633
2015 | 176.739 | - | 346.5343 | 74.2034 | 178.8599 | 26.5325 | 153.5057 |  | 346.5343 | 2949.0133 | 176.739 | 11546.9276 | - | - | - | 176.739 | - | 2373.0668 | 178.8599 | 26.5325 | 346.5343 | 346.5343 | - | 76.1754 | 178.8599 | 517.4912 | 5705.2011 | 153.5057
2016 | 189.1107 | - | 370.7917 | 79.3976 | 191.3801 | 28.3897 | - |  | 370.7917 | 3155.4442 | 189.1107 | 12355.2126 | - | - | - | 189.1107 | - | 2539.1814 | 191.3801 | 28.3897 | 370.7917 | 370.7917 | - | 81.5077 | 191.3801 | 553.7156 | 6104.5652 | -
2017 | 202.3485 | - | 396.7471 | 84.9555 | 204.7767 | 30.377 | - |  | 396.7471 | 3376.3253 | 202.3485 | 13220.0774 | - | - | - | 202.3485 | - | 2716.9241 | 204.7767 | 30.377 | 396.7471 | 396.7471 | - | 87.2133 | 204.7767 | 592.4757 | 6531.8847 | -
2018 | - | - | 428.3439 | - | - | 32.5034 | - |  | 428.3439 | 679.231 | - | 10103.9163 | - | - | 1348.3334 | - | - | 1615.0605 | - | 32.5034 | 428.3439 | 428.3439 | - | 93.3182 | - | 633.949 | 6989.1167 | -
2019 | - | - | 458.328 | - | - | 34.7786 | - |  | 458.328 | 726.7772 | - | 10811.1905 | - | - | 1442.7167 | - | - | 1728.1147 | - | 34.7786 | 458.328 | 458.328 | - | 99.8505 | - | 678.3254 | - | -
2020 | - | - | 490.4109 | - | - | - | - |  | 490.4109 | 777.6516 | - | - | - | - | 1543.7069 | - | - | 1849.0827 | - | - | 490.4109 | 490.4109 | - | 106.84 | - | 725.8082 | - | -
2021 | - | - | 524.7397 | - | - | - | - |  | 524.7397 | 832.0872 | - | - | - | - | 1651.7664 | - | - | 1978.5185 | - | - | 524.7397 | 524.7397 | - | - | - | 776.6147 | - | -
2022 | - | - | 561.4715 | - | - | - | - |  | 561.4715 | 890.3333 | - | - | - | - | 1767.39 | - | - | - | - | - | 561.4715 | 561.4715 | - | - | - | 830.9778 | - | -
HOURLY EXCEEDANCES: INVEST YEAR
Investment trigger point (MVA) | 20 | 20 | 78.77 | 139.02 | 20 | 20 | 60.4 |  | 176 | 4.24 | 20 | 9.66 | 15 | 20 | 25.1 | 111 | 15 | 35.9 | 20 | 15 | 15 | 20 | 20 | 20 | 15 | 20 | 20 | 10
Year | 2017 | 2017 | 2022 | 2017 | 2017 | 2019 | 2015 |  |  | 2022 | 2016 | 2019 | 2017 | 2023 | 2024 |  | 2016 | 2021 | 2022 | 2017 | 2015 | 2014 | 2022 | 2020 |  | 2022 | 2018
No. of hours over the trigger point (hr) | 1 | 1 | 5 | 4 | 1 | 1 | - |  |  | 2 | 1 | 2 | 1 |  |  |  | 1 | 12 | 1 |  | 2 | 1 | 1 | 1 |  | 1 | 1
Duration of Exceedance by Month INVEST YEAR (total number of hours on worst day) (hr)
January | - | - | 4 | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 2 | - |  | 2 | 1 | 1 | 1 |  | - | -
February | - | - | - | 2 | - | - | - |  |  | - | - | 2 | - |  |  |  | 1 | 3 | - |  | - | - | - | - |  | - | 1
March | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 4 | - |  | - | - | - | - |  | 1 | -
April | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
May | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
June | 1 | - | 1 | - | - | 1 | - |  |  | 1 | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
July | - | - | - | 1 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
August | - | 1 | - | - | - | - | - |  |  | 1 | - | - | 1 |  |  |  | - | - | - |  | - | - | - | - |  | - | -
September | - | - | - | 1 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
October | - | - | - | - | - | - | - |  |  | - | 1 | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
November | - | - | - | - | 1 | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
December | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | 1 |  | - | - | - | - |  | - | -
Duration of Exceedance by Month INVEST YEAR (number of consecuative hours on worst day) (hr)
January | - | - | 4 | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 2 | - |  | 2 | 1 | 1 | 1 |  | - | -
February | - | - | - | 2 | - | - | - |  |  | - | - | 2 | - |  |  |  | 1 | 3 | - |  | - | - | - | - |  | - | 1
March | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 4 | - |  | - | - | - | - |  | 1 | -
April | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
May | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
June | 1 | - | 1 | - | - | 1 | - |  |  | 1 | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
July | - | - | - | 1 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
August | - | 1 | - | - | - | - | - |  |  | 1 | - | - | 1 |  |  |  | - | - | - |  | - | - | - | - |  | - | -
September | - | - | - | 1 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
October | - | - | - | - | - | - | - |  |  | - | 1 | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
November | - | - | - | - | 1 | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
December | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | 1 |  | - | - | - | - |  | - | -
MAX EXCEEDANCE BY MONTH: INVEST YEAR (MVA)
January | - | - | 1.2409 | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 1.1427 | - |  | - | - | - | - |  | - | -
February | - | - | - | 1.7882 | - | - | - |  |  | - | - | 0.14 | - |  |  |  | - | 1.313 | - |  | - | - | - | - |  | - | -
March | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 1.8 | - |  | - | - | - | - |  | - | -
April | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
May | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
June | - | - | 2.23 | - | - | - | - |  |  | 0.06 | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
July | - | - | - | 2.98 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
August | - | - | - | - | - | - | - |  |  | 0.023564 | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
September | - | - | - | 1.4651 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
October | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
November | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
December | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
Number of days of Exceedance by Month: INVEST YEAR (days)
January | - | - | 1 | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 1 | - |  | 1 | 1 | 1 | 1 |  | - | -
February | - | - | - | 1 | - | - | - |  |  | - | - | 1 | - |  |  |  | 1 | 3 | - |  | - | - | - | - |  | - | 1
March | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | 2 | - |  | - | - | - | - |  | 1 | -
April | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
May | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
June | 1 | - | 1 | - | - | 1 | - |  |  | 1 | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
July | - | - | - | 1 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
August | - | 1 | - | - | - | - | - |  |  | 1 | - | - | 1 |  |  |  | - | - | - |  | - | - | - | - |  | - | -
September | - | - | - | 1 | - | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
October | - | - | - | - | - | - | - |  |  | - | 1 | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
November | - | - | - | - | 1 | - | - |  |  | - | - | - | - |  |  |  | - | - | - |  | - | - | - | - |  | - | -
December | - | - | - | - | - | - | - |  |  | - | - | - | - |  |  |  | - | - | 1 |  | - | - | - | - |  | - | -
HOURLY EXCEEDANCES: Year 10
Investment trigger point (MVA) | 20 | 20 | 78.77 | 139.02 | 20 | 20 | 60.4 |  | 176 | 4.24 | 20 | 9.66 | 15 | 20 | 25.1 | 111 | 15 | 35.9 | 20 | 15 | 15 | 20 | 20 | 20 | 15 | 20 | 20 | 10
Year | 2027 | 2027 | 2032 | 2027 | 2027 | 2029 | 2025 |  |  | 2032 | 2026 | 2029 | 2027 | 2033 | 2034 |  | 2026 | 2031 | 2032 | 2027 | 2025 | 2024 | 2032 | 2030 |  | 2032 | 2028
No. of hours over the trigger point (hr) | 458 | 1 | 342 | 384 | 622 | 1 | 4562 |  |  | 34 | 1 | 53 | 1 |  |  |  | 1 | 1614 | 1 |  | 6 | 1 | 1 | 1593 |  | 609 | 15
Duration of Exceedance by Month Year 10 (total number of hours on worst day) (hr)
January | 9 | - | 12 | 5 | 12 | - | 22 |  |  | - | - | - | - |  |  |  | - | 10 | - |  | 3 | 1 | 1 | 16 |  | 12 | -
February | 11 | - | 12 | 12 | 18 | - | 24 |  |  | - | - | 7 | - |  |  |  | 1 | 11 | - |  | - | - | - | 16 |  | 14 | 3
March | 6 | - | 8 | 3 | 11 | - | 24 |  |  | - | - | 4 | - |  |  |  | - | 14 | - |  | - | - | - | 15 |  | 22 | -
April | 5 | - | - | - | 1 | - | 24 |  |  | - | - | - | - |  |  |  | - | 7 | - |  | - | - | - | 4 |  | 17 | -
May | 6 | - | 5 | 11 | - | - | 24 |  |  | - | - | - | - |  |  |  | - | 13 | - |  | 2 | - | - | 8 |  | 6 | -
June | 16 | - | 9 | 16 | 4 | 1 | 24 |  |  | 6 | - | - | - |  |  |  | - | 16 | - |  | - | - | - | 15 |  | 16 | 2
July | 15 | - | 3 | 7 | - | - | 24 |  |  | 3 | - | - | - |  |  |  | - | 17 | - |  | - | - | - | 5 |  | - | -
August | 9 | 1 | - | 4 | 1 | - | 24 |  |  | 4 | - | - | 1 |  |  |  | - | 11 | - |  | - | - | - | 5 |  | - | -
September | - | - | - | 6 | - | - | 24 |  |  | - | - | - | - |  |  |  | - | 8 | - |  | - | - | - | 5 |  | - | -
October | - | - | 1 | 4 | 1 | - | 24 |  |  | - | 1 | - | - |  |  |  | - | 9 | - |  | - | - | - | 11 |  | 3 | -
November | 1 | - | - | 2 | 9 | - | 24 |  |  | - | - | - | - |  |  |  | - | 10 | - |  | - | - | - | 11 |  | - | -
December | 5 | - | 5 | 3 | 13 | - | 24 |  |  | - | - | - | - |  |  |  | - | 10 | 1 |  | - | - | - | 15 |  | 5 | 1
Duration of Exceedance by Month Year 10 (number of consecuative hours on worst day) (hr)
January | 9 | - | 12 | 3 | 12 | - | 18 |  |  | - | - | - | - |  |  |  | - | 10 | - |  | 3 | 1 | 1 | 16 |  | 12 | -
February | 11 | - | 12 | 12 | 16 | - | 24 |  |  | - | - | 7 | - |  |  |  | 1 | 11 | - |  | - | - | - | 16 |  | 14 | 2
March | 6 | - | 8 | 2 | 11 | - | 24 |  |  | - | - | 3 | - |  |  |  | - | 14 | - |  | - | - | - | 15 |  | 18 | -
April | 5 | - | - | - | 1 | - | 24 |  |  | - | - | - | - |  |  |  | - | 7 | - |  | - | - | - | 3 |  | 15 | -
May | 3 | - | 4 | 4 | - | - | 24 |  |  | - | - | - | - |  |  |  | - | 13 | - |  | 2 | - | - | 5 |  | 5 | -
June | 16 | - | 6 | 9 | 4 | 1 | 24 |  |  | 6 | - | - | - |  |  |  | - | 16 | - |  | - | - | - | 15 |  | 8 | 2
July | 15 | - | 3 | 4 | - | - | 24 |  |  | 3 | - | - | - |  |  |  | - | 17 | - |  | - | - | - | 4 |  | - | -
August | 7 | 1 | - | 2 | 1 | - | 24 |  |  | 4 | - | - | 1 |  |  |  | - | 9 | - |  | - | - | - | 4 |  | - | -
September | - | - | - | 6 | - | - | 24 |  |  | - | - | - | - |  |  |  | - | 8 | - |  | - | - | - | 4 |  | - | -
October | - | - | 1 | 3 | 1 | - | 24 |  |  | - | 1 | - | - |  |  |  | - | 9 | - |  | - | - | - | 11 |  | 3 | -
November | 1 | - | - | 2 | 9 | - | 24 |  |  | - | - | - | - |  |  |  | - | 10 | - |  | - | - | - | 11 |  | - | -
December | 5 | - | 4 | 2 | 12 | - | 24 |  |  | - | - | - | - |  |  |  | - | 10 | 1 |  | - | - | - | 15 |  | 5 | 1
MAX EXCEEDANCE BY MONTH: Year 10 (MVA)
January | 3.2056 | - | 23.2687 | 15.7612 | 4.8121 | - | 15.6462 |  |  | - | - | - | - |  |  |  | - | 14.8987 | - |  | 2.1 | - | - | 13.9 |  | 4.387 | -
February | 4.1582 | - | 19.9093 | 29.5532 | 5.5188 | - | 23.5803 |  |  | - | - | 1.34 | - |  |  |  | - | 15.1322 | - |  | - | - | - | 11.4805 |  | 6.5434 | 1.2
March | 2.9925 | - | 16.2873 | 6.1399 | 2.0405 | - | 23.8201 |  |  | - | - | 0.74975 | - |  |  |  | - | 15.8 | - |  | - | - | - | 9.6142 |  | 6.6 | -
April | 5.2331 | - | - | - | 0.32264 | - | 32.0285 |  |  | - | - | - | - |  |  |  | - | 3.1425 | - |  | - | - | - | 1.0833 |  | 5.2294 | -
May | 3.2185 | - | 14.4645 | 20.0983 | - | - | 26.7306 |  |  | - | - | - | - |  |  |  | - | 9.5774 | - |  | 1.9903 | - | - | 5.6696 |  | 4.1599 | -
June | 6.5 | - | 24.53 | 22.4063 | 1.729 | - | 25.7352 |  |  | 0.66 | - | - | - |  |  |  | - | 12.4231 | - |  | - | - | - | 11.1529 |  | 6.0126 | 0.61727
July | 5.1682 | - | 11.275 | 30.98 | - | - | 33.3805 |  |  | 0.49302 | - | - | - |  |  |  | - | 8.9993 | - |  | - | - | - | 5.9437 |  | - | -
August | 4.2533 | - | - | 19.9847 | 0.20202 | - | 30.7338 |  |  | 0.61848 | - | - | - |  |  |  | - | 12.3105 | - |  | - | - | - | 3.5923 |  | - | -
September | - | - | - | 29.1664 | - | - | 27.2515 |  |  | - | - | - | - |  |  |  | - | 7.0479 | - |  | - | - | - | 2.2533 |  | - | -
October | - | - | 2.3579 | 19.6322 | 0.0088089 | - | 23.4294 |  |  | - | - | - | - |  |  |  | - | 7.7943 | - |  | - | - | - | 3.9108 |  | 0.68315 | -
November | 0.72284 | - | - | 12.8737 | 6.2 | - | 33.8 |  |  | - | - | - | - |  |  |  | - | 7.3352 | - |  | - | - | - | 4.6338 |  | - | -
December | 3.6323 | - | 2.1701 | 14.517 | 3.5716 | - | 25.7432 |  |  | - | - | - | - |  |  |  | - | 10.7376 | - |  | - | - | - | 10.5143 |  | 1.4331 | 0.024846
Number of days of Exceedance by Month: Year 10 (days)
January | 4 | - | 10 | 12 | 19 | - | 16 |  |  | - | - | - | - |  |  |  | - | 17 | - |  | 2 | 1 | 1 | 30 |  | 9 | -
February | 6 | - | 17 | 16 | 21 | - | 18 |  |  | - | - | 11 | - |  |  |  | 1 | 20 | - |  | - | - | - | 28 |  | 13 | 5
March | 3 | - | 6 | 2 | 16 | - | 23 |  |  | - | - | 2 | - |  |  |  | - | 18 | - |  | - | - | - | 24 |  | 13 | -
April | 1 | - | - | - | 3 | - | 18 |  |  | - | - | - | - |  |  |  | - | 8 | - |  | - | - | - | 5 |  | 10 | -
May | 13 | - | 10 | 8 | - | - | 31 |  |  | - | - | - | - |  |  |  | - | 17 | - |  | 1 | - | - | 20 |  | 16 | -
June | 20 | - | 21 | 25 | 7 | 1 | 22 |  |  | 7 | - | - | - |  |  |  | - | 21 | - |  | - | - | - | 30 |  | 26 | 3
July | 19 | - | 5 | 11 | - | - | 31 |  |  | 6 | - | - | - |  |  |  | - | 24 | - |  | - | - | - | 13 |  | - | -
August | 18 | 1 | - | 8 | 1 | - | 31 |  |  | 2 | - | - | 1 |  |  |  | - | 18 | - |  | - | - | - | 13 |  | - | -
September | - | - | - | 11 | - | - | 30 |  |  | - | - | - | - |  |  |  | - | 16 | - |  | - | - | - | 4 |  | - | -
October | - | - | 1 | 8 | 1 | - | 31 |  |  | - | 1 | - | - |  |  |  | - | 21 | - |  | - | - | - | 14 |  | 3 | -
November | 2 | - | - | 2 | 8 | - | 22 |  |  | - | - | - | - |  |  |  | - | 22 | - |  | - | - | - | 19 |  | - | -
December | 5 | - | 1 | 6 | 17 | - | 11 |  |  | - | - | - | - |  |  |  | - | 16 | 1 |  | - | - | - | 18 |  | 4 | 1
LOAD PROFILE: INVEST YEAR (MVA)
Year | 2017 | 2017 | 2022 | 2017 | 2017 | 2019 | 2015 |  |  | 2022 | 2016 | 2019 | 2017 | 2023 | 2024 |  | 2016 | 2021 | 2022 | 2017 | 2015 | 2014 | 2022 | 2020 |  | 2022 | 2018
Peak load (MVA) | 20 | 20 | 81 | 142 | 20 | 20 | 60.1 |  |  | 4.3 | 20 | 9.8 | 15 | 20 | 25.3 |  | 15 | 37.7 | 20 | 15 | 15 | 20 | 20 | 20 |  | 20 | 20
Investment trigger point (MVA) | 20 | 20 | 78.77 | 139.02 | 20 | 20 | 60.4 |  | 176 | 4.24 | 20 | 9.66 | 15 | 20 | 25.1 | 111 | 15 | 35.9 | 20 | 15 | 15 | 20 | 20 | 20 | 15 | 20 | 20 | 10
PEAK DAY LOAD PROFILE: INVEST YEAR (MVA)
12 am | 13.9819 | 17.4956 | 42.4911 | 110.9904 | 11.8912 | 11.6438 | 47.4916 |  |  | 2.0451 | 11.344 | 7.0182 | 13.0487 |  |  |  | 10.2464 | 17.2941 | 7.8182 |  | 4.3952 | 8.2565 | 11.6073 | 10.7342 |  | 16.891 | 14.7978
1 am | 11.9673 | 14.6085 | 38.5622 | 100.888 | 10.641 | 10.8649 | 50.9163 |  |  | 1.6536 | 8.9993 | 6.6777 | 10.8285 |  |  |  | 10.1479 | 13.4026 | 8.6006 |  | 3.9881 | 8.7315 | 11.3449 | 9.6757 |  | 16.6143 | 14.6394
2 am | 10.3335 | 12.9877 | 37.1475 | 88.9222 | 10.0606 | 9.3859 | 49.7929 |  |  | 1.4118 | 7.6594 | 6.699 | 9.4999 |  |  |  | 10.3773 | 12.292 | 7.4127 |  | 3.8301 | 9.3107 | 10.8645 | 9.9648 |  | 16.4988 | 16.3368
3 am | 9.5993 | 11.9732 | 37.2374 | 101.5548 | 9.963 | 8.6733 | 53.4051 |  |  | 1.2918 | 7.3929 | 6.6987 | 8.6712 |  |  |  | 10.559 | 11.8493 | 7.4871 |  | 3.7625 | 9.6765 | 10.6589 | 9.2645 |  | 16.1307 | 15.0923
4 am | 9.4758 | 11.6866 | 37.9355 | 92.9064 | 10.0643 | 8.5595 | 55.2355 |  |  | 1.3822 | 7.3012 | 6.8396 | 8.3843 |  |  |  | 10.7763 | 11.8705 | 5.3733 |  | 3.7088 | 9.7271 | 10.6554 | 9.1851 |  | 15.3367 | 16.2797
5 am | 10.0596 | 11.9665 | 40.3712 | 98.5225 | 10.1309 | 9.3583 | 56.0744 |  |  | 1.5822 | 7.9505 | 7.1353 | 8.6256 |  |  |  | 11.0773 | 12.7111 | 5.9228 |  | 3.7866 | 10.0507 | 10.6802 | 8.9464 |  | 14.8286 | 15.9701
6 am | 11.9781 | 13.5237 | 45.5794 | 92.7087 | 10.3161 | 11.2883 | 50.3516 |  |  | 2.0664 | 9.541 | 7.7322 | 9.8582 |  |  |  | 11.3866 | 16.4331 | 6.6424 |  | 3.9683 | 10.9554 | 10.9381 | 9.0455 |  | 14.5021 | 15.9873
7 am | 15.525 | 17.2409 | 57.2982 | 88.4114 | 10.8734 | 14.2248 | 51.6356 |  |  | 2.7321 | 12.0916 | 7.9936 | 12.743 |  |  |  | 11.72 | 25.4195 | 8.5326 |  | 4.603 | 12.6667 | 11.2809 | 10.9514 |  | 15.508 | 14.9723
8 am | 17.9454 | 19.2672 | 66.4575 | 83.8071 | 11.6366 | 16.0918 | 53.7184 |  |  | 3.3558 | 13.8107 | 8.0347 | 14.2633 |  |  |  | 12.1912 | 28.5986 | 9.654 |  | 5.5655 | 14.1602 | 12.0652 | 12.6756 |  | 16.7103 | 15.7856
9 am | 17.5774 | 20 | 65.2316 | 80.0067 | 14.156 | 14.7483 | 55.4513 |  |  | 3.3487 | 14.066 | 8.2969 | 15 |  |  |  | 12.6964 | 30.3821 | 8.9396 |  | 6.1234 | 16.747 | 13.3784 | 14.1659 |  | 16.6766 | 15.2261
10 am | 17.4447 | 19.4398 | 63.2825 | 84.3989 | 18.1207 | 14.2871 | 55.6428 |  |  | 3.555 | 14.3186 | 8.0956 | 14.6237 |  |  |  | 13.1546 | 30.5865 | 8.8533 |  | 6.5083 | 18.6404 | 14.7765 | 15.4357 |  | 15.7539 | 14.7075
11 am | 16.9445 | 17.7739 | 60.6938 | 95.8364 | 18.6119 | 14.2458 | 55.7121 |  |  | 3.6649 | 16.9899 | 8.6684 | 13.1645 |  |  |  | 13.5537 | 32.6732 | 10.0028 |  | 6.8119 | 18.6464 | 15.8639 | 16.1117 |  | 16.0658 | 14.5849
12 pm | 16.6589 | 16.5219 | 59.1187 | 90.2084 | 18.9558 | 14.7365 | 54.1334 |  |  | 3.0893 | 20 | 9.1118 | 12.2057 |  |  |  | 13.9504 | 35.0461 | 10.6827 |  | 7.0872 | 18.7969 | 16.9426 | 17.19 |  | 15.6548 | 17.4606
1 pm | 16.6419 | 16.2885 | 58.6605 | 98.3568 | 19.1222 | 14.4405 | 53.3178 |  |  | 3.2098 | 14.0615 | 9.8 | 11.8422 |  |  |  | 14.2384 | 36.0078 | 12.7607 |  | 7.2531 | 19.153 | 19.5651 | 17.775 |  | 17.3263 | 17.8755
2 pm | 16.1912 | 15.105 | 58.8693 | 105.7994 | 19.7508 | 14.8443 | 51.6311 |  |  | 2.8743 | 11.6438 | 9.7438 | 10.8839 |  |  |  | 14.6925 | 36.9639 | 12.8137 |  | 7.6435 | 20 | 20 | 18.3847 |  | 18.4166 | 17.9426
3 pm | 16.3049 | 15.4061 | 56.7956 | 110.4186 | 20 | 14.9643 | 55.5212 |  |  | 3.2975 | 11.2625 | 9.6094 | 11.2346 |  |  |  | 15 | 37.7 | 13.9439 |  | 7.7665 | 19.6333 | 19.3081 | 18.7233 |  | 18.8779 | 18.9553
4 pm | 16.7773 | 14.9057 | 58.9036 | 105.6776 | 19.7028 | 14.8838 | 53.5603 |  |  | 3.7557 | 10.7193 | 9.1142 | 11.0458 |  |  |  | 3.4296 | 36.1124 | 13.716 |  | 7.9142 | 18.7673 | 19.9632 | 19.2404 |  | 18.6648 | 18.8543
5 pm | 18.0621 | 15.1608 | 63.4131 | 142 | 13.7899 | 16.3466 | 60.1 |  |  | 3.9558 | 11.0988 | 8.6698 | 11.1732 |  |  |  | 3.2703 | 34.1459 | 13.3373 |  | 7.8388 | 18.3932 | 19.4641 | 19.9831 |  | 19.0851 | 19.465
6 pm | 20 | 16.5449 | 76.0103 | 122.9573 | 13.4928 | 20 | 55.9993 |  |  | 4.3 | 10.6378 | 8.0981 | 12.2841 |  |  |  | 3.4272 | 29.9884 | 14.0237 |  | 7.3764 | 17.2976 | 16.8673 | 20 |  | 20 | 20
7 pm | 18.8744 | 17.0219 | 81 | 111.7635 | 13.4945 | 18.7512 | 54.3619 |  |  | 4.1559 | 10.7449 | 6.7111 | 12.4753 |  |  |  | 3.5899 | 30.0283 | 17.9137 |  | 7.1686 | 15.2702 | 17.6056 | 19.4346 |  | 19.7437 | 16.9022
8 pm | 17.6895 | 16.9149 | 76.3122 | 115.9259 | 13.8702 | 17.2387 | 56.6424 |  |  | 3.8813 | 10.6636 | 6.293 | 12.4982 |  |  |  | 3.675 | 28.7377 | 20 |  | 9.5343 | 11.2116 | 15.4579 | 19.3169 |  | 18.6449 | 18.0526
9 pm | 17.5097 | 18.0803 | 72.2114 | 111.2942 | 13.2783 | 16.371 | 55.2079 |  |  | 3.815 | 11.0663 | 6.7826 | 13.4484 |  |  |  | 3.51 | 26.9866 | 16.0772 |  | 15 | 10.1581 | 14.5784 | 17.9039 |  | 18.3614 | 17.8045
10 pm | 16.0967 | 18.2832 | 63.6676 | 96.3105 | 12.319 | 15.1849 | 52.8994 |  |  | 3.6494 | 10.8655 | 6.4617 | 13.5442 |  |  |  | 3.4057 | 24.7115 | 13.8178 |  | 15 | 8.8653 | 13.1034 | 15.4903 |  | 17.5926 | 17.0037
11 pm | 15.0341 | 16.9079 | 53.412 | 101.0543 | 11.3009 | 13.9976 | 56.3473 |  |  | 2.5176 | 10.651 | 5.8195 | 12.4386 |  |  |  | 3.1428 | 20.3357 | 11.9913 |  | 14.5341 | 7.7905 | 12.357 | 13.4069 |  | 16.2804 | 16.3702
LOAD PROFILE: Year 10 (MVA)
Year | 2027 | 2027 | 2032 | 2027 | 2027 | 2029 | 2025 |  |  | 2032 | 2026 | 2029 | 2027 | 2033 | 2034 |  | 2026 | 2031 | 2032 | 2027 | 2025 | 2024 | 2032 | 2030 |  | 2032 | 2028
Peak load (MVA) | 26.5 | 20 | 103.3 | 170 | 26.2 | 20 | 94.2 |  |  | 4.9 | 20 | 11 | 15 | 20 | 27.3 |  | 15 | 51.7 | 20 | 15.5 | 17.1 | 20 | 20 | 33.9 |  | 26.6 | 21.2
Investment trigger point (MVA) | 20 | 20 | 78.77 | 139.02 | 20 | 20 | 60.4 |  | 176 | 4.24 | 20 | 9.66 | 15 | 20 | 25.1 | 111 | 15 | 35.9 | 20 | 15 | 15 | 20 | 20 | 20 | 15 | 20 | 20 | 10
PEAK DAY LOAD PROFILE: Year 10 (MVA)
12 am | 18.526 | 17.4956 | 54.1893 | 132.8758 | 15.5775 | 11.6438 | 74.4378 |  |  | 2.3304 | 11.344 | 7.8776 | 13.0487 |  |  |  | 10.2464 | 23.7163 | 7.8182 |  | 5.0105 | 8.2565 | 11.6073 | 18.1945 |  | 22.465 | 15.6857
1 am | 15.8566 | 14.6085 | 49.1787 | 120.7813 | 13.9397 | 10.8649 | 79.8056 |  |  | 1.8843 | 8.9993 | 7.4954 | 10.8285 |  |  |  | 10.1479 | 18.3796 | 8.6006 |  | 4.5464 | 8.7315 | 11.3449 | 16.4004 |  | 22.097 | 15.5177
2 am | 13.6919 | 12.9877 | 47.3746 | 106.4561 | 13.1793 | 9.3859 | 78.0448 |  |  | 1.6088 | 7.6594 | 7.5193 | 9.4999 |  |  |  | 10.3773 | 16.8566 | 7.4127 |  | 4.3663 | 9.3107 | 10.8645 | 16.8903 |  | 21.9434 | 17.317
3 am | 12.7191 | 11.9732 | 47.4891 | 121.5797 | 13.0516 | 8.6733 | 83.7065 |  |  | 1.4721 | 7.3929 | 7.5189 | 8.6712 |  |  |  | 10.559 | 16.2496 | 7.4871 |  | 4.2893 | 9.6765 | 10.6589 | 15.7034 |  | 21.4539 | 15.9979
4 am | 12.5554 | 11.6866 | 48.3795 | 111.226 | 13.1842 | 8.5595 | 86.5754 |  |  | 1.5751 | 7.3012 | 7.6771 | 8.3843 |  |  |  | 10.7763 | 16.2786 | 5.3733 |  | 4.228 | 9.7271 | 10.6554 | 15.5687 |  | 20.3978 | 17.2565
5 am | 13.3289 | 11.9665 | 51.4857 | 117.9494 | 13.2715 | 9.3583 | 87.8904 |  |  | 1.8029 | 7.9505 | 8.009 | 8.6256 |  |  |  | 11.0773 | 17.4314 | 5.9228 |  | 4.3167 | 10.0507 | 10.6802 | 15.1642 |  | 19.722 | 16.9283
6 am | 15.871 | 13.5237 | 58.1277 | 110.9892 | 13.5141 | 11.2883 | 78.9205 |  |  | 2.3547 | 9.541 | 8.679 | 9.8582 |  |  |  | 11.3866 | 22.5356 | 6.6424 |  | 4.5239 | 10.9554 | 10.9381 | 15.3322 |  | 19.2878 | 16.9465
7 am | 20.5706 | 17.2409 | 73.0729 | 105.8447 | 14.2441 | 14.2248 | 80.933 |  |  | 3.1133 | 12.0916 | 8.9725 | 12.743 |  |  |  | 11.72 | 34.859 | 8.5326 |  | 5.2474 | 12.6667 | 11.2809 | 18.5626 |  | 20.6256 | 15.8707
8 am | 23.7777 | 19.2672 | 84.7538 | 100.3324 | 15.2439 | 16.0918 | 84.1975 |  |  | 3.8241 | 13.8107 | 9.0186 | 14.2633 |  |  |  | 12.1912 | 39.2188 | 9.654 |  | 6.3446 | 14.1602 | 12.0652 | 21.4852 |  | 22.2247 | 16.7327
9 am | 23.29 | 20 | 83.1904 | 95.7827 | 18.5443 | 14.7483 | 86.9136 |  |  | 3.816 | 14.066 | 9.3128 | 15 |  |  |  | 12.6964 | 41.6646 | 8.9396 |  | 6.9807 | 16.747 | 13.3784 | 24.0111 |  | 22.1798 | 16.1396
10 am | 23.1142 | 19.4398 | 80.7047 | 101.0409 | 23.7381 | 14.2871 | 87.2138 |  |  | 4.051 | 14.3186 | 9.0869 | 14.6237 |  |  |  | 13.1546 | 41.9448 | 8.8533 |  | 7.4195 | 18.6404 | 14.7765 | 26.1635 |  | 20.9527 | 15.5899
11 am | 22.4514 | 17.7739 | 77.4033 | 114.7338 | 24.3816 | 14.2458 | 87.3225 |  |  | 4.1763 | 16.9899 | 9.7298 | 13.1645 |  |  |  | 13.5537 | 44.8065 | 10.0028 |  | 7.7656 | 18.6464 | 15.8639 | 27.3093 |  | 21.3675 | 15.46
12 pm | 22.073 | 16.5219 | 75.3946 | 107.996 | 24.8321 | 14.7365 | 84.848 |  |  | 3.5204 | 20 | 10.2275 | 12.2057 |  |  |  | 13.9504 | 48.0606 | 10.6827 |  | 8.0795 | 18.7969 | 16.9426 | 29.137 |  | 20.8208 | 18.5082
1 pm | 22.0506 | 16.2885 | 74.8103 | 117.7511 | 25.0501 | 14.4405 | 83.5697 |  |  | 3.6577 | 14.0615 | 11 | 11.8422 |  |  |  | 14.2384 | 49.3794 | 12.7607 |  | 8.2685 | 19.153 | 19.5651 | 30.1286 |  | 23.044 | 18.948
2 pm | 21.4533 | 15.105 | 75.0765 | 126.6612 | 25.8736 | 14.8443 | 80.9259 |  |  | 3.2754 | 11.6438 | 10.9369 | 10.8839 |  |  |  | 14.6925 | 50.6906 | 12.8137 |  | 8.7136 | 20 | 20 | 31.162 |  | 24.494 | 19.0191
3 pm | 21.604 | 15.4061 | 72.4319 | 132.1913 | 26.2 | 14.9643 | 87.0233 |  |  | 3.7576 | 11.2625 | 10.7861 | 11.2346 |  |  |  | 15 | 51.7 | 13.9439 |  | 8.8538 | 19.6333 | 19.3081 | 31.736 |  | 25.1076 | 20.0926
4 pm | 22.2299 | 14.9057 | 75.1203 | 126.5154 | 25.8107 | 14.8838 | 83.9498 |  |  | 4.2797 | 10.7193 | 10.2302 | 11.0458 |  |  |  | 3.4296 | 49.5228 | 13.716 |  | 9.0222 | 18.7673 | 19.9632 | 32.6124 |  | 24.8242 | 19.9856
5 pm | 23.9322 | 15.1608 | 80.8713 | 170 | 18.0647 | 16.3466 | 94.2 |  |  | 4.5078 | 11.0988 | 9.7314 | 11.1732 |  |  |  | 3.2703 | 46.826 | 13.3373 |  | 8.9363 | 18.3932 | 19.4641 | 33.8714 |  | 25.3831 | 20.6329
6 pm | 26.5 | 16.5449 | 96.9365 | 147.2024 | 17.6756 | 20 | 87.7726 |  |  | 4.9 | 10.6378 | 9.0897 | 12.2841 |  |  |  | 3.4272 | 41.1247 | 14.0237 |  | 8.409 | 17.2976 | 16.8673 | 33.9 |  | 26.6 | 21.2
7 pm | 25.0086 | 17.0219 | 103.3 | 133.8014 | 17.6779 | 18.7512 | 85.2061 |  |  | 4.7358 | 10.7449 | 7.5328 | 12.4753 |  |  |  | 3.5899 | 41.1794 | 17.9137 |  | 8.1722 | 15.2702 | 17.6056 | 32.9416 |  | 26.2591 | 17.9164
8 pm | 23.4386 | 16.9149 | 97.3216 | 138.7845 | 18.1699 | 17.2387 | 88.7806 |  |  | 4.4228 | 10.6636 | 7.0635 | 12.4982 |  |  |  | 3.675 | 39.4096 | 20 |  | 10.8691 | 11.2116 | 15.4579 | 32.7421 |  | 24.7977 | 19.1358
9 pm | 23.2003 | 18.0803 | 92.0918 | 133.2396 | 17.3946 | 16.371 | 86.5322 |  |  | 4.3473 | 11.0663 | 7.6132 | 13.4484 |  |  |  | 3.51 | 37.0082 | 16.0772 |  | 17.1 | 10.1581 | 14.5784 | 30.3472 |  | 24.4207 | 18.8728
10 pm | 21.3282 | 18.2832 | 81.1959 | 115.3013 | 16.1379 | 15.1849 | 82.9138 |  |  | 4.1586 | 10.8655 | 7.2529 | 13.5442 |  |  |  | 3.4057 | 33.8883 | 13.8178 |  | 17.1 | 8.8653 | 13.1034 | 26.256 |  | 23.3982 | 18.0239
11 pm | 19.9202 | 16.9079 | 68.1167 | 120.9805 | 14.8042 | 13.9976 | 88.3181 |  |  | 2.8689 | 10.651 | 6.5321 | 12.4386 |  |  |  | 3.1428 | 27.8874 | 11.9913 |  | 16.5689 | 7.7905 | 12.357 | 22.7247 |  | 21.653 | 17.3524
SUMMER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 111 | 75.8 | 176 | 264 | 74.8 | 30 | 140 | 10 | 176 | 7.8 | 27.7 | 11 | 15.2 | 20 | 30 | 111 | 15 | 55 | 20 | 15.5 | 15 | 5 | 20 | 69.8 | 15 | 44 | 22 | 20
n-1 capacity (MVA) | 45.7 | 42.7 | 104 | 208 | 40 | 14 | 70 | 10 | 104 | 4.4 | 15.6 | 6.5 | 7.6 | 9.2 | 15 | 45.7 | 8.2 | 33.1 | 20 | 7 | 7.7 | 2.5 | 8.5 | 46.6 | - | 26 | 13 | 10
Secure capacity (MVA) | 45.7 | 42.7 | 104 | 208 | 40 | 30 | 70 | 10 | 176 | 7.8 | 15.6 | 6.5 | 15.2 | 20 | 15 | 111 | 8.2 | 33.1 | 20 | 7 | 7.7 | 2.5 | 8.5 | 46.6 | - | 26 | 13 | 10
Reliability requirement | N-1 | N-1 | N-1 | N-1 | N-1 | N | N-1 |  |  | N | N-1 | N-1 | N | N | N-1 | N | N-1 | N-1 | N | N-1 | N-1 | N-1 | N-1 | N-1 | N-1 | N-1 | N-1 | N-1
Actual/forecast peak load: Summer (MVA)
2010 | 33.866 | 16.2 | 59.4 | 121.5 | 33.6 | 27.4 | 58.7 |  | 59.4 | 3.2 | 13.2 | 8.6 | 12 | 9.5 | 25.3 | 33.866 | 2.1 | 24.6 | 1 | 7.4 | 8 | 6.8 | 10.3 | 36.6 | 8.5 | 14.9 | 10.3 | 7.3
2011 | 29.3 | 13.3 | 68 | 115.2 | 32.6 | 26.3 | 54.9 |  | 68 | 2.8 | 11.7 | 6.1 | 10.5 | 8.8 | 20.8 | 29.3 | 9.4 | 23.7 | 1 | 7.8 | 8.8 | 5.8 | 10.3 | 36.1 | 6.3 | 15.2 | 9.8 | 7.2
2012 | 28.9 | 14 | 58.7 | 128.9 | 32.9 | 27.5 | 56.5 |  | 58.7 | 3.3 | 12.1 | 9.2 | 10.7 | 10.9 | 22.9 | 28.9 | 7.7 | 20.8 | 0.6 | 10 | 7.9 | 5.4 | 10.7 | 39 | 6.1 | 12.4 | 11.9 | 8.7
2013 | 28.8 | 13.3 | 63.8 | 131.8 | 36.1 | 19.6 | 61.3 |  | 63.8 | 3.1 | 11.9 | 9.8 | 11.3 | 11.3 | 22.6 | 28.8 | 9.3 | 24.4 | 0.6 | 10.9 | 10.2 | 6.6 | 10.8 | 42.1 | 7.2 | 14.7 | 12.6 | 9.7
2014 | 28.3 | 12.8 | 64.9 | 138.3 | 35.3 | 19.4 | 62.6 |  | 64.9 | 3 | 10 | 9.5 | 11 | 11.1 | 21.9 | 28.3 | 3.5 | 24.5 | 0.6 | 10.7 | 10.2 | 6.6 | 10.5 | 41.4 | 7 | 16 | 13.1 | 9.7
2015 | 29 | 12.9 | 66.5 | 138.9 | 35.6 | 19.9 | 63.4 |  | 66.5 | 3.1 | 10.5 | 9.6 | 11 | 11.5 | 22.1 | 29 | 3.6 | 25.7 | 0.6 | 11 | 10.7 | 6.9 | 10.7 | 42.5 | 7 | 16.1 | 13.7 | 10.1
2016 | 29.3 | 12.9 | 67.5 | 138.3 | 35.5 | 19.6 | 68.7 |  | 67.5 | 3.1 | 11 | 9.6 | 11 | 11.7 | 22.2 | 29.3 | 3.7 | 26.6 | 0.6 | 11.2 | 11 | 7.1 | 10.8 | 43.3 | 7 | 16.1 | 14 | 10.5
2017 | 30.4 | 13.1 | 69.9 | 142 | 36.3 | 20.6 | 71.5 |  | 69.9 | 3.3 | 11.7 | 9.7 | 11.2 | 12.2 | 22.7 | 30.4 | 3.8 | 28.3 | 0.6 | 11.7 | 11.6 | 7.5 | 11.2 | 45 | 7.1 | 16.4 | 14.7 | 11.1
2018 | 30.7 | 13.1 | 70.6 | 141.9 | 36.1 | 21 | 89.1 |  | 70.6 | 3.3 | 12.2 | 9.7 | 11.2 | 12.4 | 22.7 | 30.7 | 3.9 | 29.2 | 0.6 | 11.8 | 11.9 | 7.7 | 11.2 | 45.6 | 7.1 | 16.4 | 15.1 | 11.3
2019 | 31.7 | 13.3 | 72.9 | 145 | 36.7 | 21.4 | 90.7 |  | 72.9 | 3.4 | 12.9 | 9.8 | 11.3 | 12.8 | 23.1 | 31.7 | 4 | 30.8 | 0.6 | 12.2 | 12.4 | 8.1 | 11.5 | 47.1 | 7.2 | 16.6 | 15.7 | 11.9
2020 | 33.4 | 13.8 | 76.7 | 151.5 | 38.1 | 22.7 | 94.5 |  | 76.7 | 3.6 | 14 | 10.2 | 11.8 | 13.6 | 24.1 | 33.4 | 4.2 | 33.2 | 0.7 | 13 | 13.3 | 8.7 | 12.1 | 49.9 | 7.5 | 17.3 | 16.7 | 12.7
2021 | 34.4 | 13.9 | 78.8 | 154.2 | 38.6 | 23.1 | 95.9 |  | 78.8 | 3.7 | 14.8 | 10.3 | 11.9 | 14 | 24.5 | 34.4 | 4.4 | 34.8 | 0.7 | 13.3 | 13.8 | 9 | 12.4 | 51.4 | 7.6 | 17.5 | 17.3 | 13.2
2022 | 35.4 | 14.1 | 81 | 156.9 | 39.1 | 23.7 | 97.3 |  | 81 | 3.8 | 15.7 | 10.4 | 12 | 14.4 | 24.9 | 35.4 | 4.5 | 36.5 | 0.7 | 13.8 | 14.3 | 9.4 | 12.6 | 52.9 | 7.7 | 17.7 | 18 | 13.8
Average Growth (MVA/yr)
2012 to 2017 | 0.3 | -0.18 | 2.24 | 2.62 | 0.68 | -1.38 | 3 |  | 2.24 | - | -0.08 | 0.1 | 0.1 | 0.26 | -0.04 | 0.3 | -0.78 | 1.5 | - | 0.34 | 0.74 | 0.42 | 0.1 | 1.2 | 0.2 | 0.8 | 0.56 | 0.48
2017 to 2022 | 1 | 0.2 | 2.22 | 2.98 | 0.56 | 0.62 | 5.16 |  | 2.22 | 0.1 | 0.8 | 0.14 | 0.16 | 0.44 | 0.44 | 1 | 0.14 | 1.64 | 0.02 | 0.42 | 0.54 | 0.38 | 0.28 | 1.58 | 0.12 | 0.26 | 0.66 | 0.54
2022 onwards | 0.3 | -0.18 | 2.23 | 2.62 | 0.68 | -0.87143 | 2.3 |  | 2.23 | 0.05 | -0.275 | 0.085714 | 0.1 | 0.35 | 0.2 | 0.65 | -1 | 1.5556 | 0.01 | 0.34 | 0.93333 | 0.6 | 0.19 | 1.3625 | 0.16 | 0.53 | 0.53333 | 0.51
WINTER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 111 | 75.8 | 176 | 264 | 74.8 | 30 | 140 | 10 | 176 | 7.8 | 27.7 | 11 | 15.2 | 20 | 30 | 111 | 15 | 55 | 20 | 15.5 | 15 | 5 | 20 | 69.8 | 15 | 44 | 22 | 20
n-1 capacity (MVA) | 45.7 | 42.7 | 104 | 208 | 40 | 14 | 70 | 10 | 104 | 4.4 | 15.6 | 6.5 | 7.6 | 9.2 | 15 | 45.7 | 8.2 | 33.1 | 20 | 7 | 7.7 | 2.5 | 8.5 | 46.6 | - | 26 | 13 | 10
Secure capacity (MVA) | 45.7 | 42.7 | 104 | 208 | 40 | 30 | 70 | 10 | 176 | 7.8 | 15.6 | 6.5 | 15.2 | 20 | 15 | 111 | 8.2 | 33.1 | 20 | 7 | 7.7 | 2.5 | 8.5 | 46.6 | - | 26 | 13 | 10
Reliability requirement | N-1 | N-1 | N-1 | N-1 | N-1 | N | N-1 |  |  | N | N-1 | N-1 | N | N | N-1 | N | N-1 | N-1 | N | N-1 | N-1 | N-1 | N-1 | N-1 | N-1 | N-1 | N-1 | N-1
Actual/forecast peak load: Winter (MVA)
2010 | 30.3 | 13.7 | 59.3 | 111.8 | 27.7 | 26.8 | 54.6 |  | 59.3 | 3.4 | 11.2 | 5.1 | 11.6 | 7.6 | 17.8 | 30.3 | 5.9 | 22 | 1 | 1.8 | 6.6 | 4.2 | 10.1 | 31.5 | 6.9 | 11.5 | 7.6 | 5.7
2011 | 32.1 | 13.2 | 56.6 | 120.4 | 27.3 | 27.9 | 53.2 |  | 56.6 | 3.4 | 12.1 | 3.9 | 11 | 8.6 | 18.6 | 32.1 | 7.1 | 23.6 | 0.6 | 8.3 | 7.2 | 4.8 | 10.3 | 33 | 5.6 | 14.9 | 8.6 | 5.7
2012 | 33.8 | 14 | 59.6 | 126.5 | 25.5 | 22.9 | 58.3 |  | 59.6 | 3.7 | 13.4 | 4.1 | 12.5 | 8.9 | 20.3 | 33.8 | 7.4 | 25.3 | 0.7 | 9 | 8.3 | 5 | 10.7 | 32.4 | 6.2 | 15.9 | 9.1 | 6.1
2013 | 34.7 | 14.1 | 64 | 127.3 | 25.7 | 20.4 | 61.9 |  | 64 | 3.7 | 14 | 4.1 | 12.6 | 9.1 | 20.6 | 34.7 | 3.5 | 26.5 | 0.7 | 9.3 | 8.7 | 5.2 | 11 | 33.7 | 6.2 | 18.7 | 9.9 | 6.3
2014 | 34 | 13.7 | 63 | 133.5 | 24.8 | 19.9 | 59.9 |  | 63 | 3.6 | 12.1 | 3.9 | 12.2 | 9 | 20 | 34 | 3.4 | 26.6 | 0.7 | 9.1 | 8.6 | 5.1 | 10.9 | 33.4 | 6 | 18.3 | 9.8 | 6.4
2015 | 34.6 | 13.7 | 64.4 | 131.1 | 24.9 | 20.1 | 60.1 |  | 64.4 | 3.7 | 12.5 | 3.9 | 12.2 | 9.2 | 20.2 | 34.6 | 3.5 | 27.7 | 0.7 | 9.2 | 8.9 | 5.2 | 11.3 | 34.4 | 6 | 18.6 | 10 | 6.6
2016 | 35.1 | 13.8 | 65.5 | 130.8 | 24.5 | 20.2 | 66.3 |  | 65.5 | 3.7 | 13 | 3.9 | 12.2 | 9.4 | 20.4 | 35.1 | 3.6 | 28.7 | 0.7 | 9.4 | 9.1 | 5.2 | 11.5 | 35.4 | 6 | 18.8 | 10.2 | 6.9
2017 | 36.1 | 14 | 67.7 | 133 | 24.8 | 20.7 | 84.4 |  | 67.7 | 3.8 | 13.6 | 4 | 12.3 | 9.7 | 20.9 | 36.1 | 3.7 | 30.3 | 0.7 | 9.6 | 9.5 | 5.4 | 12 | 36.8 | 6.1 | 19.4 | 10.5 | 7.2
2018 | 36.8 | 14.1 | 69.4 | 134.3 | 25 | 21 | 85.1 |  | 69.4 | 3.8 | 14.2 | 4 | 12.4 | 10 | 21.2 | 36.8 | 3.8 | 31.6 | 0.7 | 9.8 | 9.9 | 5.5 | 12.4 | 38 | 6.1 | 19.8 | 10.8 | 7.5
2019 | 37.9 | 14.4 | 71.7 | 136.9 | 25.4 | 21.5 | 86.6 |  | 71.7 | 3.9 | 14.9 | 4.1 | 12.6 | 10.4 | 21.7 | 37.9 | 3.9 | 33.3 | 0.7 | 10.2 | 10.3 | 5.7 | 12.8 | 39.7 | 6.2 | 20.3 | 11.1 | 7.9
2020 | 40.1 | 15 | 76.1 | 143.2 | 26.5 | 22.6 | 90.3 |  | 76.1 | 4.1 | 16 | 4.2 | 13.1 | 11 | 22.8 | 40.1 | 4.1 | 36 | 0.7 | 10.8 | 11 | 6 | 13.7 | 42.4 | 6.5 | 21.5 | 11.8 | 8.4
2021 | 41.2 | 15.3 | 78.5 | 145.7 | 26.9 | 23.1 | 91.7 |  | 78.5 | 4.2 | 16.7 | 4.3 | 13.2 | 11.4 | 23.3 | 41.2 | 4.3 | 37.7 | 0.7 | 11.1 | 11.4 | 6.2 | 14.2 | 44.1 | 6.5 | 22 | 12.2 | 8.8
2022 | 42 | 15.4 | 80.4 | 147.2 | 27.2 | 23.4 | 92.4 |  | 80.4 | 4.3 | 17.4 | 4.3 | 13.3 | 11.7 | 23.6 | 42 | 4.4 | 39.3 | 0.7 | 11.3 | 11.8 | 6.4 | 14.6 | 45.4 | 6.6 | 22.5 | 12.5 | 9.2
Average Growth (MVA/yr)
2012 to 2017 | 0.46 | - | 1.62 | 1.3 | -0.14 | -0.44 | 5.22 |  | 1.62 | 0.02 | 0.04 | -0.02 | -0.04 | 0.16 | 0.12 | 0.46 | -0.74 | 1 | - | 0.12 | 0.24 | 0.08 | 0.26 | 0.88 | -0.02 | 0.7 | 0.28 | 0.22
2017 to 2022 | 1.18 | 0.28 | 2.54 | 2.84 | 0.48 | 0.54 | 1.6 |  | 2.54 | 0.1 | 0.76 | 0.06 | 0.2 | 0.4 | 0.54 | 1.18 | 0.14 | 1.8 | - | 0.34 | 0.46 | 0.2 | 0.52 | 1.72 | 0.1 | 0.62 | 0.4 | 0.4
2022 onwards | 0.46 | - | 2.08 | 1.3 | -0.14 | -0.2 | 0.6 |  | 2.08 | 0.06 | -0.1 | - | -0.04 | 0.28 | 0.33 | 0.82 | -0.95 | 1.3778 | - | 0.12 | 0.2 | 0.05 | 0.39 | 1.25 | 0.04 | 0.66 | 0.28333 | 0.31

## Vic
GENERAL INPUTS
Display name of asset | NKA-CME line | SMTS-KLO line | BLTS-BMH line | KGTS-SHL line | WPD-TQY line | KTS-MLN line | RWTS-BRA-BWR line | DPTS-MLN line | TTS-NEI-NH-WT line | MWTS-LGA-FTR line | Wemen TS | Bendigo TS | Keilor TS | Ballarat TS | Wangaratta ZS | Cobram East ZS | Bendigo ZS | Watsonia ZS | Epping ZS | Torquay ZS | Ferntree Gully ZS | Bacchus Marsh ZS | Myrtleford ZS | Bairnsdale ZS | Lang Lang ZS | Warragul ZS | Boundary Bend ZS | Melton ZS | Merbein ZS | Maryborough ZS | Geelong East ZS | Sale ZS | Swan Hill ZS | Eaglehawke ZS | Numurkah ZS | Werribee ZS | St Albans ZS | Thomastown ZS
Short name of asset | NKA-CME | SMTS-KLO | BLTS-BMH | KGTS-SHL | WPD-TQY | KTS-MLN | RWTS-BRA-BWR-RWTS | DPTS-MLN | TTS-NEI-NH-WT-TTS | MWTS-LGA-FTR-MWTS | WETS | BETS | KTS | BATS | WN | CME | BGO | WT | EPG | TQY | FGY | BMH | MYT | BDL | LLG | WGL | BBD | MLN | MBN | MRO | GLE | SLE | SHL | EHK | NKA | WBE | SA | TT
Full name of asset | Numurkah ZS - Cobram East ZS StLi 66kV | South Morang TS - Kalkallo ZS Radial Line | Brooklyn TS - Bacchus Marsh ZS StLi Circuit 66kV | Kerang TS - Swan Hill ZS StLi #1 Circuit | Waurn Ponds ZS - Torquay ZS StLi | Keilor TS - Melton ZS StLi Circuit 66kV | Ringwood TS - Boronia ZS - Bayswater ZS Circuit | Deer Park TS - Melton ZS StLi 66kV | Thomastown TS - Nilsens ZS - North Heidelberg ZS - Watsonia ZS Circuit | Morwell TS - Leongatha ZS - Foster ZS Circuit | Wemen TS | Bendigo TS 66kV and 22kV | Keilor TS | Ballarat TS 66kV | Wangaratta | Cobram East ZS 22kV | Bendigo ZS 22kV | Watsonia | Epping | Torquay ZS | Ferntree Gully | Bacchus Marsh ZS 22kV | Myrtleford | Bairnsdale | Lang Lang | Warragul | Boundary Bend ZS 22kV | Melton ZS 22kV | Merbein ZS 22kV | Maryborough ZS 22kV | Geelong East ZS 22kV | Sale | Swan Hill ZS 22kV | Eaglehawke ZS 22kV | Numurkah ZS | Werribee ZS 22kV | St Albans ZS 22kV | Thomastown
Region | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic | Vic
Asset type | Stli | Stli | Stli | Stli | Stli | Stli | Stli | Stli | Stli | Stli | bar: WETS to TT
Provider | Powercor | SPAusnet | Powercor | Powercor | Powercor | Powercor | SPAusnet | Powercor | SPAusnet | SPAusnet | Powercor | Powercor | Powercor | Powercor | SPAusnet | Powercor | Powercor | SPAusnet | SPAusnet | Powercor | SPAusnet | Powercor | SPAusnet | SPAusnet | SPAusnet | SPAusnet | Powercor | Powercor | Powercor | Powercor | Powercor | SPAusnet | Powercor | Powercor | Powercor | Powercor | Powercor | SPAusnet
Associated Tx | [5 empty] | KTS |  |  |  |  | BGO: BETS; BMH: BATS; MLN: KTS; MRO: BETS; EHK: BETS
Associated STL | [10 empty] | BATS: BLTS-BMH; CME: NKA-CME; WT: TTS-NEI-NH-WT-TTS; EPG: SMTS-KLO; TQY: WPD-TQY; BMH: BLTS-BMH; MLN: DPTS-MLN; SLE: MWTS-LGA-FTR-MWTS; SHL: KGTS-SHL; NKA: NKA-CME
Latitude | -35.9721 | -37.6525 | -37.7011 | -35.3468 | -38.3147 | -37.6888 | -37.7635 | -37.6888 | -37.7134 | -38.4735 | -34.7868 | -36.7865 | -37.7397 | -37.569 | -36.3645 | -35.9721 | -36.7721 | -37.7134 | -37.6526 | -38.3147 | -37.8935 | -37.7011 | -36.5652 | -37.8084 | -38.2674 | -38.1538 | -34.717 | -37.6888 | -34.1763 | -37.051 | -38.1812 | -38.1014 | -35.3468 | -36.7374 | -36.0709 | -37.892 | -37.7416 | -37.6909
Longitude | 145.6953 | 145.0263 | 144.407 | 143.5213 | 144.3238 | 144.5846 | 145.3581 | 144.5846 | 145.0857 | 145.9472 | 142.5251 | 144.2527 | 144.8448 | 143.9205 | 146.3143 | 145.6953 | 144.276 | 145.0857 | 145.0261 | 144.3238 | 145.2924 | 144.407 | 146.7033 | 147.6477 | 145.5566 | 145.9427 | 143.1517 | 144.5846 | 142.0782 | 143.7534 | 144.3801 | 147.0957 | 143.5213 | 144.2773 | 145.4499 | 144.6615 | 144.8239 | 145.0108
POE value | Unknown |  | Unknown | Unknown | Unknown | Unknown |  | Unknown |  |  | 50 | Unknown | Unknown | Unknown |  | Unknown | Unknown |  |  | Unknown |  | Unknown |  |  |  |  | Unknown | Unknown | Unknown | Unknown | Unknown |  | Unknown | Unknown | Unknown | Unknown | Unknown
Season to use
Land available | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Notes for outputsheet | New #2 line | KLO-DRN 66kV line | Three investments - $2.4m in 2013, $3.8m in 2014 and $1.4m in 2015, combined and attributed to the year of the largest investment (2014). | Reconductor #1 line in stages | WPD-TQY line convert 22kV to 66kV. 1st investment of $1.7M in 2013 is assumed to occur, only $1.4M in 2016 included. | Five new 66kV lines | Construct new CYN-BWR 66kV line | Establish two 66kV lines. Deer Park TS will be created to transfer Sunshine ZS from the Keilor TS network to alleviate load at risk at Keilor TS. | Reconductor TTS-WT 66kV line | Re-conductor 22km of MWTS-LGA No.2 66kV line | Wemen TS (WETS)was commissioned in October 2012, with a single 70 MVA transformer. A combination of single transformer outage and load growth could result in unacceptable loss of load. | Install two new 75 MVA 230/22 kV transformers. Value of network investment is given as an annual figure in TCPR. | Five 150MVA transformers and four 66kV buses. Note two stages of investment - $6m in 2012/14 for new 100MVAR capacitor bank. In 2015-16, a new $125m TS at Deer Park and associated StLi"s. | New 220/66kV transformer | Install new 20/33MVA transformer | New 22kV capacitors are expected to be installed after 2017 | Install 22kV feeder from BETS | Reconductor TTS-WT 66kV line | New 66kV line | Establish new Torquay ZS (co-ordinates for town) | Install a fifth 20/33 transformer in 2015 | Augment BMH & MLN 22kV network to increase load transfer away capapcity to adjacent ZS. Additional 22kV feeder at MLN followed by an additional transformer at MLN. | Install transformer cooling fans. Adjust overnight hot water heating load timing. Planned completion <2014 | Install new 20/33 MVA transformer in 2015 | Install 2nd 20/33 transformer in 2015 | Install new 20/33 MVA transformer | Additional transformer | Additional transformer. Investment spread over two years $0.3m in 2014 and $3.2m in 2016. | Additional 66/22kV transformer | Additional transformer | Upgrade two transformers | No.1 Transformer replaced with new 20/33 MVA unit |  | Additional transformer |  | Establish new Truganina ZS to offload SA, SU, LV, LVN & WBE | Augment 22kV transformer isolators | Install fourth 20/33 MVA transformer by 2016
Maximum connection | 44.9 |  | 47.4667 | 58.2 |  | 112.5 |  |  |  |  | 77 | 350 | 509 | 341 | 66 | 40.5 | 66 | 109 | 99 |  | 93 | 27 | 18.8 | 48 | 19.9 | 84 | 33 | 66 | 26 | 27 | 40.5 | 39.5 | 40.5 | 54 | 39.5 | 99 | 93 | 84
NETWORK INVESTMENT
Proposed investment ($m) | 11 | 13.5 | 8 | 4.1 | 1.4 | 6.2 | 3.4 | 17.6 | 2.2 | 6.5 | 12 | 28 | 147 | 15.5 | 4.5 | 1.7 | 1 |  |  | 11.64 | 6 | 0.8 | 0.5 | 6 | 3.5 | 6 | 4 | 3.6 | 3 | 4 | 10 | 5 |  | 6 |  | 15 | 0.2 | 6
Proposed investment year | 2017 | 2016 | 2015 | 2016 | 2016 | 2017 | 2014 | 2015 | 2014 | 2017 | 2021 | 2014 | 2018 | 2022 | 2018 | 2017 | 2014 |  |  | 2016 | 2018 | 2014 | 2014 | 2015 | 2018 | 2019 | 2015 | 2016 | 2015 | 2019 | 2015 | 2015 |  | 2016 |  | 2015 | 2015 | 2019
Annual Deferral Value of system in 2014 ($/kVA/yr) | 1142.0785 |  | 120.3018 | 144.926 |  | 143.0482 |  |  |  |  | 316.8313 | 390.7419 | 434.1172 | 229.4806 | 898.9823 | 1335.1287 | 423.7172 |  |  |  | 216.7759 | 389.7974 | 445.1667 | - | 475.4617 | 137.0062 | 378.2215 | 495.7812 | 164.2277 | 844.1672 | 305.9144 | 904.4426 | 144.926 | 566.152 | 1142.0785 | 242.827 | 5.0737 | 139.0063
Type of constraint | Growth, None |  | Growth, None | Growth, None |  | Growth, None |  |  |  |  | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None |  | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | Growth, None | None | Growth, None | None | Growth, None | Growth, None | Growth, None
Constraint season | Summer |  | Summer | Summer |  | Summer |  |  |  |  | Summer | Summer | Summer | Summer | Summer | Summer | Summer |  |  |  | Summer | Summer | Winter | Summer | BOTH | BOTH (Summer) | Summer | Summer | Summer | Summer | Summer | Summer |  | Summer |  | Summer | Summer | Summer
Capacity Shortfall: INVEST YEAR (MVA) | 0.7 |  | 5.5333 | 2.2 |  | 3.15 |  |  |  |  | 0.8 | 6.38 | 21.3333 | 3.4444 | 0.34 | 0.64 | 2.7 | - | - |  | 1.88 | 1.78 | 0.1 | - | 0.5 | 2.78 | 0.88 | 4.54 | 1.52 | 0.56 | 2.72 | 0.46 | - | 2.66 | - | 5.14 | 3.28 | 2.74
Capacity Shortfall: Year 10 (MVA) | 7.7 |  | 60.8333 | 24.2 |  | 34.65 |  |  |  |  | 15.3 | 71.03 | 212.6667 | 37.6111 | 3.74 | 7.04 | 39.2 | - | - |  | 20.68 | 25.18 | 1.1 | - | 5.5 | 30.58 | 11.1133 | 52.365 | 19.2867 | 6.16 | 30.82 | 5.26 | - | 28.21 | - | 63.6733 | 38.0133 | 30.14
SYSTEM INVESTMENT
Investment for system ($m) | 11 | 13.5 | 8 | 4.1 | 1.4 | 6.2 | 3.4 | 17.6 | 2.2 | 6.5 | 12 | 28 | 147 | 15.5 | 4.5 | 12.7 | 29 | 2.2 | 13.5 | 13.04 | 6 | 24.3 | 0.5 | 6 | 3.5 | 6 | 4 | 168.2 | 3 | 32 | 10 | 11.5 | 4.1 | 34 | 11 | 15 | 0.2 | 6
Investment for ZS ($m) | [14 empty] | 4.5 | 1.7 | 1 |  |  | 11.64 | 6 | 0.8 | 0.5 | 6 | 3.5 | 6 | 4 | 3.6 | 3 | 4 | 10 | 5 |  | 6 |  | 15 | 0.2 | 6
Investment for Stli ($m) | 11 | 13.5 | 8 | 4.1 | 1.4 | 6.2 | 3.4 | 17.6 | 2.2 | 6.5 | CME: 11; WT: 2.2; EPG: 13.5; TQY: 1.4; BMH: 8; MLN: 17.6; SLE: 6.5; SHL: 4.1; NKA: 11
Investment for TS ($m) | [10 empty] | WETS: 12; BETS: 28; KTS: 147; BATS: 15.5; BGO: 28; BMH: 15.5; MLN: 147; MRO: 28; EHK: 28
Investment year for system | 2017 | 2016 | 2015 | 2016 | 2016 | 2017 | 2014 | 2015 | 2014 | 2017 | 2021 | 2014 | 2018 | 2022 | 2018 | 2017 | 2014 | 2014 | 2016 | 2016 | 2018 | 2014 | 2014 | 2015 | 2018 | 2019 | 2015 | 2015 | 2015 | 2014 | 2015 | 2015 | 2016 | 2014 | 2017 | 2015 | 2015 | 2019
Investment year for ZS | [14 empty] | 2018 | 2017 | 2014 |  |  | 2016 | 2018 | 2014 | 2014 | 2015 | 2018 | 2019 | 2015 | 2016 | 2015 | 2019 | 2015 | 2015 |  | 2016 |  | 2015 | 2015 | 2019
Investment year for Stli | 2017 | 2016 | 2015 | 2016 | 2016 | 2017 | 2014 | 2015 | 2014 | 2017 | CME: 2017; WT: 2014; EPG: 2016; TQY: 2016; BMH: 2015; MLN: 2015; SLE: 2017; SHL: 2016; NKA: 2017
Investment year for TS | [10 empty] | WETS: 2021; BETS: 2014; KTS: 2018; BATS: 2022; BGO: 2014; BMH: 2022; MLN: 2018; MRO: 2014; EHK: 2014
System capacity shortfall: INVEST YEAR (MVA) | 0.7 |  | 5.5333 | 2.2 |  | 3.15 |  |  |  |  | 0.8 | 6.38 | 21.3333 | 3.4444 | 0.34 | 0.7 | 6.38 | - | - |  | 1.88 | 5.5333 | 0.1 | - | 0.5 | 2.78 | 0.88 | 21.3333 | 1.52 | 6.38 | 2.72 | 0.46 | 2.2 | 6.38 | 0.7 | 5.14 | 3.28 | 2.74
ZS capacity shortfall: INVEST YEAR (MVA) | [14 empty] | 0.34 | 0.64 | 2.7 | - | - |  | 1.88 | 1.78 | 0.1 | - | 0.5 | 2.78 | 0.88 | 4.54 | 1.52 | 0.56 | 2.72 | 0.46 | - | 2.66 | - | 5.14 | 3.28 | 2.74
Stli capacity shortfall: INVEST YEAR (MVA) | 0.7 |  | 5.5333 | 2.2 |  | 3.15 |  |  |  |  | CME: 0.7; BMH: 5.5333; SHL: 2.2; NKA: 0.7
TS capacity shortfall: INVEST YEAR (MVA) | [10 empty] | WETS: 0.8; BETS: 6.38; KTS: 21.3333; BATS: 3.4444; BGO: 6.38; BMH: 3.4444; MLN: 21.3333; MRO: 6.38; EHK: 6.38
System capacity shortfall: Year 10 (MVA) | 7.7 |  | 60.8333 | 24.2 |  | 34.65 |  |  |  |  | 15.3 | 71.03 | 212.6667 | 37.6111 | 3.74 | 7.7 | 71.03 | - | - |  | 20.68 | 60.8333 | 1.1 | - | 5.5 | 30.58 | 11.1133 | 212.6667 | 19.2867 | 71.03 | 30.82 | 5.26 | 24.2 | 71.03 | 7.7 | 63.6733 | 38.0133 | 30.14
ZS capacity shortfall: Year 10 (MVA) | [14 empty] | 3.74 | 7.04 | 39.2 | - | - |  | 20.68 | 25.18 | 1.1 | - | 5.5 | 30.58 | 11.1133 | 52.365 | 19.2867 | 6.16 | 30.82 | 5.26 | - | 28.21 | - | 63.6733 | 38.0133 | 30.14
Stli capacity shortfall: Year 10 (MVA) | 7.7 |  | 60.8333 | 24.2 |  | 34.65 |  |  |  |  | CME: 7.7; BMH: 60.8333; SHL: 24.2; NKA: 7.7
TS capacity shortfall: Year 10 (MVA) | [10 empty] | WETS: 15.3; BETS: 71.03; KTS: 212.6667; BATS: 37.6111; BGO: 71.03; BMH: 37.6111; MLN: 212.6667; MRO: 71.03; EHK: 71.03
NET PRESENT VALUE IN 2014 ($m)
of system | 9.5444 | 11.2474 | 6.3696 | 3.4159 | 1.1664 | 5.3796 | 2.5727 | 14.0131 | 1.6647 | 5.6399 | 11.8155 | 21.1866 | 132.2914 | 15.6433 | 4.0497 | 11.0194 | 21.9433 | 1.6647 | 11.2474 | 10.8642 | 5.3996 | 22.6182 | 0.37833 | 4.7772 | 3.1498 | 5.5806 | 3.1848 | 149.3038 | 2.3886 | 24.907 | 7.962 | 9.6209 | 3.4159 | 26.1855 | 9.5444 | 11.943 | 0.15924 | 5.5806
of asset | 9.5444 | 11.2474 | 6.3696 | 3.4159 | 1.1664 | 5.3796 | 2.5727 | 14.0131 | 1.6647 | 5.6399 | 11.8155 | 21.1866 | 132.2914 | 15.6433 | 4.0497 | 1.475 | 0.75667 |  |  | 9.6978 | 5.3996 | 0.60533 | 0.37833 | 4.7772 | 3.1498 | 5.5806 | 3.1848 | 2.9993 | 2.3886 | 3.7204 | 7.962 | 3.981 |  | 4.9989 |  | 11.943 | 0.15924 | 5.5806
of linked ZS | [14 empty] | 4.0497 | 1.475 | 0.75667 |  |  | 9.6978 | 5.3996 | 0.60533 | 0.37833 | 4.7772 | 3.1498 | 5.5806 | 3.1848 | 2.9993 | 2.3886 | 3.7204 | 7.962 | 3.981 |  | 4.9989 |  | 11.943 | 0.15924 | 5.5806
of linked Stli | 9.5444 | 11.2474 | 6.3696 | 3.4159 | 1.1664 | 5.3796 | 2.5727 | 14.0131 | 1.6647 | 5.6399 | CME: 9.5444; WT: 1.6647; EPG: 11.2474; TQY: 1.1664; BMH: 6.3696; MLN: 14.0131; SLE: 5.6399; SHL: 3.4159; NKA: 9.5444
of linked TS | [10 empty] | WETS: 11.8155; BETS: 21.1866; KTS: 132.2914; BATS: 15.6433; BGO: 21.1866; BMH: 15.6433; MLN: 132.2914; MRO: 21.1866; EHK: 21.1866
AVAILABLE CAPACITY (MVA)
2010 | 4.2 |  | 22.1333 | 11 |  | 18.9 |  |  |  |  | 17.1 | 19.68 | 152.6667 | 38.2778 | 2.38 | 3.84 | 11.9 |  |  |  | 13.16 | 7.58 | -4.1 | -4.32 | 1 | 22.24 | 4.38 | 24.64 | 7.62 | 4.48 | 11.42 | 1.96 |  | 12.46 |  | 24.84 | 14.28 | 21.92
2011 | 3.5 |  | 16.6 | 8.8 |  | 15.75 |  |  |  |  | 15 | 13.3 | 129.6667 | 34.7778 | -3.6 | 2.06 | -2.9 |  |  |  | 0.2 | 1.72 | -4.2 | -3.68 | 1.5 | 16.38 | 6.42 | 13.56 | 2.28 | 2.76 | -1.32 | 3.64 |  | 3.04 |  | 15.56 | 7.22 | 11.14
2012 | 2.8 |  | 11.0667 | 6.6 |  | 12.6 |  |  |  |  | 12.9 | 6.92 | 106.6667 | 31.2778 | 1.7 | 2.56 | 6.5 |  |  |  | 9.4 | 4.02 | 0.1 | -3.48 | 2.5 | 16.68 | 2.62 | 15.56 | 4.58 | 3.36 | 5.98 | 1.04 |  | 7.14 |  | 14.56 | 7.72 | 16.44
2013 | 2.1 |  | 5.4667 | 4.8 |  | 10.3 |  |  |  |  | 8.8 | 0.32 | 68.6667 | 28.3778 | 1.7 | 0.46 | -1.6 |  |  |  | 1.3 | -0.78 | -3.5527e-15 | 2.12 | 1.7 | 9.58 | 0.82 | 2.66 | -0.02 | 2.16 | 3.78 | 0.34 |  | 0.74 |  | -0.44 | 1.82 | 8.24
2014 | 1.5 |  | 0.066667 | 3 |  | 6.7 |  |  |  |  | 6.4 | -6.38 | 38.6667 | 24.1778 | 1.2 | 0.16 | -2.7 |  |  |  | 1 | -1.78 | -0.1 | 1.22 | 1.3 | 7.88 | -0.18 | 0.36 | -0.72 | 1.76 | -0.52 | -0.06 |  | -0.36 |  | -2.24 | -0.68 | 6.84
2015 | 0.8 |  | -5.5333 | 0.7 |  | 3.3 |  |  |  |  | 4.8 | -12.78 | 22.6667 | 20.6778 | 0.8 | -0.14 | -3.8 |  |  |  | 0.7 | -2.78 | -0.2 | 0.42 | 0.9 | 6.18 | -0.88 | -2.04 | -1.52 | 1.36 | -2.72 | -0.46 |  | -1.56 |  | -5.14 | -3.28 | 5.54
2016 | 7.1054e-15 |  | -11.0333 | -2.2 |  | 2.8422e-14 |  |  |  |  | 3.5 | -18.78 | 4.6667 | 17.0778 | 0.4 | -0.34 | -5.8 |  |  |  | 0.3 | -3.78 | -0.3 | -0.48 | 0.5 | 4.48 | -1.38 | -4.54 | -2.22 | 0.96 | -6.12 | -0.86 |  | -2.66 |  | -8.04 | -5.98 | 4.14
2017 | -0.7 |  | -16.6 | -4.4 |  | -3.15 |  |  |  |  | 2.4 | -24.98 | -8.3333 | 13.7778 | -1.4211e-14 | -0.64 | -7 |  |  |  | -1.4211e-14 | -4.88 | -0.4 | -1.38 | - | 2.78 | -1.78 | -7.14 | -3.02 | 0.56 | -7.62 | -1.26 |  | -6.16 |  | -11.14 | -8.68 | 2.74
2018 | -1.4 |  | -22.1333 | -6.6 |  | -6.3 |  |  |  |  | 1.6 | -31.28 | -21.3333 | 9.7778 | -0.34 | -1.28 | -11.6 |  |  |  | -1.88 | -7.78 | -0.5 | -0.08 | -0.5 | - | -2.9467 | -12.165 | -5.0533 | - | -10.52 | -1.76 |  | -8.61 |  | -17.7067 | -12.3467 | -
2019 | -2.1 |  | -27.6667 | -8.8 |  | -9.45 |  |  |  |  | 0.8 | -37.68 | -35.3333 | 7.2778 | -0.68 | -1.92 | -16.2 |  |  |  | -3.76 | -10.68 | -0.6 | 1.22 | -1 | -2.78 | -4.1133 | -17.19 | -7.0867 | -0.56 | -13.42 | -2.26 |  | -11.06 |  | -24.2733 | -16.0133 | -2.74
2020 | -2.8 |  | -33.2 | -11 |  | -12.6 |  |  |  |  | - | -44.28 | -48.3333 | 3.7778 | -1.02 | -2.56 | -20.8 |  |  |  | -5.64 | -13.58 | -0.7 | 2.52 | -1.5 | -5.56 | -5.28 | -22.215 | -9.12 | -1.12 | -16.32 | -2.76 |  | -13.51 |  | -30.84 | -19.68 | -5.48
2021 | -3.5 |  | -38.7333 | -13.2 |  | -15.75 |  |  |  |  | -0.8 | -51.08 | -63.3333 | 0.27778 | -1.36 | -3.2 | -25.4 |  |  |  | -7.52 | -16.48 | -0.8 | 3.82 | -2 | -8.34 | -6.4467 | -27.24 | -11.1533 | -1.68 | -19.22 | -3.26 |  | -15.96 |  | -37.4067 | -23.3467 | -8.22
2022 | -4.2 |  | -44.2667 | -15.4 |  | -18.9 |  |  |  |  | -1.6 | -58.23 | -115 | -3.4444 | -1.7 | -3.84 | -30 |  |  |  | -9.4 | -19.38 | -0.9 | 5.12 | -2.5 | -11.12 | -7.6133 | -32.265 | -13.1867 | -2.24 | -22.12 | -3.76 |  | -18.41 |  | -43.9733 | -27.0133 | -10.96
ANNUAL DEFERRAL VALUES or ADV
ADV OF Asset ($/kVA/year)
2010 | 871.2862 |  | 91.7776 | 110.5633 |  | 109.1308 |  |  |  |  | 241.7091 | 298.0951 | 331.186 | 175.0697 | 685.8293 | 147.2771 | 25.1567 |  |  |  | 165.3773 | 30.5272 | 339.6155 | - | 362.7275 | 104.5214 | 288.5433 | 47.0432 | 125.2886 | 345.916 | 233.3806 | 689.995 |  | 133.8196 |  | 185.2516 | 3.8707 | 106.0472
2011 | 932.2762 |  | 98.2021 | 118.3028 |  | 116.77 |  |  |  |  | 258.6288 | 318.9618 | 354.369 | 187.3246 | 733.8373 | 157.5865 | 26.9177 |  |  |  | 176.9537 | 32.6641 | 363.3886 | - | 388.1184 | 111.8379 | 308.7414 | 50.3362 | 134.0588 | 370.1301 | 249.7173 | 738.2946 |  | 143.1869 |  | 198.2192 | 4.1417 | 113.4705
2012 | 997.5356 |  | 105.0762 | 126.584 |  | 124.9438 |  |  |  |  | 276.7328 | 341.2891 | 379.1748 | 200.4373 | 785.2059 | 168.6175 | 28.8019 |  |  |  | 189.3404 | 34.9506 | 388.8258 | - | 415.2867 | 119.6665 | 330.3533 | 53.8597 | 143.4429 | 396.0392 | 267.1975 | 789.9752 |  | 153.21 |  | 212.0945 | 4.4316 | 121.4135
2013 | 1067.3631 |  | 112.4316 | 135.4448 |  | 133.6899 |  |  |  |  | 296.1041 | 365.1793 | 405.717 | 214.4679 | 840.1703 | 180.4207 | 30.818 |  |  |  | 202.5943 | 37.3972 | 416.0436 | - | 444.3568 | 128.0432 | 353.478 | 57.6299 | 153.4839 | 423.7619 | 285.9013 | 845.2735 |  | 163.9347 |  | 226.9411 | 4.7418 | 129.9124
2014 | 1142.0785 |  | 120.3018 | 144.926 |  | 143.0482 |  |  |  |  | 316.8313 | 390.7419 | 434.1172 | 229.4806 | 898.9823 | 193.0502 | 32.9753 |  |  |  | 216.7759 | 40.015 | 445.1667 | - | 475.4617 | 137.0062 | 378.2215 | 61.664 | 164.2277 | 453.4253 | 305.9144 | 904.4426 |  | 175.4101 |  | 242.827 | 5.0737 | 139.0063
2015 | 1222.024 |  | 128.7229 | 155.0708 |  | 153.0616 |  |  |  |  | 339.0095 | - | 464.5054 | 245.5443 | 961.911 | 206.5637 | - |  |  |  | 231.9502 | - | - | - | 508.744 | 146.5966 | 404.697 | 65.9805 | 175.7237 | 485.165 | 327.3284 | 967.7536 |  | 187.6888 |  | 259.8249 | 5.4289 | 148.7367
2016 | 1307.5656 |  | - | 165.9258 |  | 163.7759 |  |  |  |  | 362.7402 | - | 497.0208 | 262.7324 | 1029.2448 | 221.0232 | - |  |  |  | 248.1867 | - | - | - | 544.3561 | 156.8584 | - | 70.5991 | - | 519.1266 | - | - |  | 200.8271 |  | - | - | 159.1483
2017 | 1399.0952 |  | - | - |  | 175.2402 |  |  |  |  | 388.132 | - | 531.8123 | 281.1237 | 1101.2919 | 236.4948 | - |  |  |  | 265.5598 | - | - | - | 582.4611 | 167.8385 | - | - | - | 555.4654 | - | - |  | - |  | - | - | 170.2887
2018 | - |  | - | - |  | - |  |  |  |  | 1090.1658 | - | 613.4953 | 305.654 | 1178.3824 | - | - |  |  |  | 284.1489 | - | - | - | 623.2333 | 179.5872 | - | - | - | 594.348 | - | - |  | - |  | - | - | 182.2089
2019 | - |  | - | - |  | - |  |  |  |  | 1166.4774 | - | - | 327.0497 | - | - | - |  |  |  | - | - | - | - | - | 192.1583 | - | - | - | 635.9524 | - | - |  | - |  | - | - | 194.9635
2020 | - |  | - | - |  | - |  |  |  |  | 1248.1308 | - | - | 349.9432 | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - |  | - |  | - | - | -
2021 | - |  | - | - |  | - |  |  |  |  | 1335.5 | - | - | 374.4393 | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - |  | - |  | - | - | -
2022 | - |  | - | - |  | - |  |  |  |  | - | - | - | 400.65 | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - |  | - |  | - | - | -
ADV OF LINKED Stli ($/kVA/year)
2010 | 871.2862 |  | 91.7776 | 110.5633 |  | 109.1308 |  |  |  |  | CME: 871.2862; BMH: 91.7776; SHL: 110.5633; NKA: 871.2862
2011 | 932.2762 |  | 98.2021 | 118.3028 |  | 116.77 |  |  |  |  | CME: 932.2762; BMH: 98.2021; SHL: 118.3028; NKA: 932.2762
2012 | 997.5356 |  | 105.0762 | 126.584 |  | 124.9438 |  |  |  |  | CME: 997.5356; BMH: 105.0762; SHL: 126.584; NKA: 997.5356
2013 | 1067.3631 |  | 112.4316 | 135.4448 |  | 133.6899 |  |  |  |  | CME: 1067.3631; BMH: 112.4316; SHL: 135.4448; NKA: 1067.3631
2014 | 1142.0785 |  | 120.3018 | 144.926 |  | 143.0482 |  |  |  |  | CME: 1142.0785; BMH: 120.3018; SHL: 144.926; NKA: 1142.0785
2015 | 1222.024 |  | 128.7229 | 155.0708 |  | 153.0616 |  |  |  |  | CME: 1222.024; BMH: 128.7229; SHL: 155.0708; NKA: 1222.024
2016 | 1307.5656 |  | - | 165.9258 |  | 163.7759 |  |  |  |  | CME: 1307.5656; BMH: -; SHL: 165.9258; NKA: 1307.5656
2017 | 1399.0952 |  | - | - |  | 175.2402 |  |  |  |  | CME: 1399.0952; BMH: -; SHL: -; NKA: 1399.0952
2018 | - |  | - | - |  | - | bar: CME; BMH; SHL; NKA
2019 | - |  | - | - |  | - | bar: CME; BMH; SHL; NKA
2020 | - |  | - | - |  | - | bar: CME; BMH; SHL; NKA
2021 | - |  | - | - |  | - | bar: CME; BMH; SHL; NKA
2022 | - |  | - | - |  | - | bar: CME; BMH; SHL; NKA
ADV OF LINKED TS ($/kVA/year)
2010 | [10 empty] | WETS: 241.7091; BETS: 298.0951; KTS: 331.186; BATS: 175.0697; BGO: 298.0951; BMH: 175.0697; MLN: 331.186; MRO: 298.0951; EHK: 298.0951
2011 | [10 empty] | WETS: 258.6288; BETS: 318.9618; KTS: 354.369; BATS: 187.3246; BGO: 318.9618; BMH: 187.3246; MLN: 354.369; MRO: 318.9618; EHK: 318.9618
2012 | [10 empty] | WETS: 276.7328; BETS: 341.2891; KTS: 379.1748; BATS: 200.4373; BGO: 341.2891; BMH: 200.4373; MLN: 379.1748; MRO: 341.2891; EHK: 341.2891
2013 | [10 empty] | WETS: 296.1041; BETS: 365.1793; KTS: 405.717; BATS: 214.4679; BGO: 365.1793; BMH: 214.4679; MLN: 405.717; MRO: 365.1793; EHK: 365.1793
2014 | [10 empty] | WETS: 316.8313; BETS: 390.7419; KTS: 434.1172; BATS: 229.4806; BGO: 390.7419; BMH: 229.4806; MLN: 434.1172; MRO: 390.7419; EHK: 390.7419
2015 | [10 empty] | WETS: 339.0095; BETS: -; KTS: 464.5054; BATS: 245.5443; BGO: -; BMH: 245.5443; MLN: 464.5054; MRO: -; EHK: -
2016 | [10 empty] | WETS: 362.7402; BETS: -; KTS: 497.0208; BATS: 262.7324; BGO: -; BMH: 262.7324; MLN: 497.0208; MRO: -; EHK: -
2017 | [10 empty] | WETS: 388.132; BETS: -; KTS: 531.8123; BATS: 281.1237; BGO: -; BMH: 281.1237; MLN: 531.8123; MRO: -; EHK: -
2018 | [10 empty] | WETS: 1090.1658; BETS: -; KTS: 613.4953; BATS: 305.654; BGO: -; BMH: 305.654; MLN: 613.4953; MRO: -; EHK: -
2019 | [10 empty] | WETS: 1166.4774; BETS: -; KTS: -; BATS: 327.0497; BGO: -; BMH: 327.0497; MLN: -; MRO: -; EHK: -
2020 | [10 empty] | WETS: 1248.1308; BETS: -; KTS: -; BATS: 349.9432; BGO: -; BMH: 349.9432; MLN: -; MRO: -; EHK: -
2021 | [10 empty] | WETS: 1335.5; BETS: -; KTS: -; BATS: 374.4393; BGO: -; BMH: 374.4393; MLN: -; MRO: -; EHK: -
2022 | [10 empty] | WETS: -; BETS: -; KTS: -; BATS: 400.65; BGO: -; BMH: 400.65; MLN: -; MRO: -; EHK: -
ADV OF SYSTEM ($/kVA/year)
2010 | 871.2862 |  | 91.7776 | 110.5633 |  | 109.1308 |  |  |  |  | 241.7091 | 298.0951 | 331.186 | 175.0697 | 685.8293 | 1018.5633 | 323.2518 |  |  |  | 165.3773 | 297.3746 | 339.6155 | - | 362.7275 | 104.5214 | 288.5433 | 378.2291 | 125.2886 | 644.0111 | 233.3806 | 689.995 | 110.5633 | 431.9147 | 871.2862 | 185.2516 | 3.8707 | 106.0472
2011 | 932.2762 |  | 98.2021 | 118.3028 |  | 116.77 |  |  |  |  | 258.6288 | 318.9618 | 354.369 | 187.3246 | 733.8373 | 1089.8627 | 345.8795 |  |  |  | 176.9537 | 318.1908 | 363.3886 | - | 388.1184 | 111.8379 | 308.7414 | 404.7052 | 134.0588 | 689.0919 | 249.7173 | 738.2946 | 118.3028 | 462.1487 | 932.2762 | 198.2192 | 4.1417 | 113.4705
2012 | 997.5356 |  | 105.0762 | 126.584 |  | 124.9438 |  |  |  |  | 276.7328 | 341.2891 | 379.1748 | 200.4373 | 785.2059 | 1166.1531 | 370.091 |  |  |  | 189.3404 | 340.4641 | 388.8258 | - | 415.2867 | 119.6665 | 330.3533 | 433.0345 | 143.4429 | 737.3283 | 267.1975 | 789.9752 | 126.584 | 494.4991 | 997.5356 | 212.0945 | 4.4316 | 121.4135
2013 | 1067.3631 |  | 112.4316 | 135.4448 |  | 133.6899 |  |  |  |  | 296.1041 | 365.1793 | 405.717 | 214.4679 | 840.1703 | 1247.7838 | 395.9974 |  |  |  | 202.5943 | 364.2966 | 416.0436 | - | 444.3568 | 128.0432 | 353.478 | 463.3469 | 153.4839 | 788.9413 | 285.9013 | 845.2735 | 135.4448 | 529.1141 | 1067.3631 | 226.9411 | 4.7418 | 129.9124
2014 | 1142.0785 |  | 120.3018 | 144.926 |  | 143.0482 |  |  |  |  | 316.8313 | 390.7419 | 434.1172 | 229.4806 | 898.9823 | 1335.1287 | 423.7172 |  |  |  | 216.7759 | 389.7974 | 445.1667 | - | 475.4617 | 137.0062 | 378.2215 | 495.7812 | 164.2277 | 844.1672 | 305.9144 | 904.4426 | 144.926 | 566.152 | 1142.0785 | 242.827 | 5.0737 | 139.0063
2015 | 1222.024 |  | 128.7229 | 155.0708 |  | 153.0616 |  |  |  |  | 339.0095 | - | 464.5054 | 245.5443 | 961.911 | 1428.5877 | - |  |  |  | 231.9502 | 374.2672 | - | - | 508.744 | 146.5966 | 404.697 | 530.4859 | 175.7237 | 485.165 | 327.3284 | 967.7536 | 155.0708 | 187.6888 | 1222.024 | 259.8249 | 5.4289 | 148.7367
2016 | 1307.5656 |  | - | 165.9258 |  | 163.7759 |  |  |  |  | 362.7402 | - | 497.0208 | 262.7324 | 1029.2448 | 1528.5888 | - |  |  |  | 248.1867 | 262.7324 | - | - | 544.3561 | 156.8584 | - | 567.6199 | - | 519.1266 | - | - | 165.9258 | 200.8271 | 1307.5656 | - | - | 159.1483
2017 | 1399.0952 |  | - | - |  | 175.2402 |  |  |  |  | 388.132 | - | 531.8123 | 281.1237 | 1101.2919 | 1635.59 | - |  |  |  | 265.5598 | 281.1237 | - | - | 582.4611 | 167.8385 | - | 531.8123 | - | 555.4654 | - | - | - | - | 1399.0952 | - | - | 170.2887
2018 | - |  | - | - |  | - |  |  |  |  | 1090.1658 | - | 613.4953 | 305.654 | 1178.3824 | - | - |  |  |  | 284.1489 | 305.654 | - | - | 623.2333 | 179.5872 | - | 613.4953 | - | 594.348 | - | - | - | - | - | - | - | 182.2089
2019 | - |  | - | - |  | - |  |  |  |  | 1166.4774 | - | - | 327.0497 | - | - | - |  |  |  | - | 327.0497 | - | - | - | 192.1583 | - | - | - | 635.9524 | - | - | - | - | - | - | - | 194.9635
2020 | - |  | - | - |  | - |  |  |  |  | 1248.1308 | - | - | 349.9432 | - | - | - |  |  |  | - | 349.9432 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2021 | - |  | - | - |  | - |  |  |  |  | 1335.5 | - | - | 374.4393 | - | - | - |  |  |  | - | 374.4393 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2022 | - |  | - | - |  | - |  |  |  |  | - | - | - | 400.65 | - | - | - |  |  |  | - | 400.65 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOURLY EXCEEDANCES: INVEST YEAR
Investment trigger point (MVA) | 44.9 |  | 47.4667 | 58.2 |  | 112.5 |  |  |  |  | 60.2 | 248.52 | 499.6667 | 209.1778 | 43.9 | 38.56 | 48.3 | 109 | 99 |  | 69.2 | 26.92 | 18.8 | 53.12 | 19.9 | 65.08 | 24.42 | 59.96 | 28.58 | 24.66 | 47.18 | 27.54 | 36.7 | 52.94 | 30.5 | 100.96 | 91.52 | 86.14
Year | 2017 |  | 2015 | 2016 |  | 2017 |  |  |  |  | 2021 | 2014 | 2018 | 2022 | 2018 | 2017 | 2014 |  |  |  | 2018 | 2014 | 2014 | 2015 | 2018 | 2019 | 2015 | 2016 | 2015 | 2019 | 2015 | 2015 |  | 2016 |  | 2015 | 2015 | 2019
No. of hours over the trigger point (hr) | [10 empty] | WETS: 3; WN: 2; FGY: 3; MYT: 1; BDL: -; LLG: 1; WGL: 2; SLE: 2; TT: 8
Duration of Exceedance by Month INVEST YEAR (total number of hours on worst day) (hr)
January | [10 empty] | WETS: 2; WN: 2; FGY: -; MYT: -; BDL: -; LLG: 1; WGL: -; SLE: 2; TT: -
February | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: -; SLE: -; TT: 2
March | [10 empty] | WETS: -; WN: -; FGY: 3; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 4
April | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
May | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
August | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
September | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
October | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
November | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
December | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
Duration of Exceedance by Month INVEST YEAR (number of consecuative hours on worst day) (hr)
January | [10 empty] | WETS: 2; WN: 2; FGY: -; MYT: -; BDL: -; LLG: 1; WGL: -; SLE: 1; TT: -
February | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: -; SLE: -; TT: 2
March | [10 empty] | WETS: -; WN: -; FGY: 3; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 4
April | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
May | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
August | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
September | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
October | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
November | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
December | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
MAX EXCEEDANCE BY MONTH: INVEST YEAR (MVA)
January | [10 empty] | WETS: 0.8; WN: 0.34; FGY: -; MYT: -; BDL: -; LLG: 0.5; WGL: -; SLE: 0.46; TT: -
February | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: -; SLE: -; TT: 2.6944
March | [10 empty] | WETS: -; WN: -; FGY: 1.88; MYT: -; BDL: -; LLG: -; WGL: 2.78; SLE: -; TT: 2.74
April | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
May | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | [10 empty] | WETS: -; WN: -; FGY: -; MYT: 0.1; BDL: -; LLG: -; WGL: -; SLE: -; TT: -
August | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
September | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
October | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
November | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
December | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: -; SLE: -; TT: 1.2233
Number of days of Exceedance by Month: INVEST YEAR (days)
January | [10 empty] | WETS: 2; WN: 1; FGY: -; MYT: -; BDL: -; LLG: 1; WGL: -; SLE: 1; TT: -
February | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
March | [10 empty] | WETS: -; WN: -; FGY: 1; MYT: -; BDL: -; LLG: -; WGL: 1; SLE: -; TT: 2
April | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
May | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
August | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
September | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
October | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
November | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
December | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
HOURLY EXCEEDANCES: Year 10
Investment trigger point (MVA) | 44.9 |  | 47.4667 | 58.2 |  | 112.5 |  |  |  |  | 60.2 | 248.52 | 499.6667 | 209.1778 | 43.9 | 38.56 | 48.3 | 109 | 99 |  | 69.2 | 26.92 | 18.8 | 53.12 | 19.9 | 65.08 | 24.42 | 59.96 | 28.58 | 24.66 | 47.18 | 27.54 | 36.7 | 52.94 | 30.5 | 100.96 | 91.52 | 86.14
Year | 2027 |  | 2025 | 2026 |  | 2027 |  |  |  |  | 2031 | 2024 | 2028 | 2032 | 2028 | 2027 | 2024 |  |  |  | 2028 | 2024 | 2024 | 2025 | 2028 | 2029 | 2025 | 2026 | 2025 | 2029 | 2025 | 2025 |  | 2026 |  | 2025 | 2025 | 2029
No. of hours over the trigger point (hr) | [10 empty] | WETS: 252; WN: 15; FGY: 102; MYT: 2; BDL: -; LLG: 40; WGL: 279; SLE: 24; TT: 754
Duration of Exceedance by Month Year 10 (total number of hours on worst day) (hr)
January | [10 empty] | WETS: 21; WN: 7; FGY: 10; MYT: -; BDL: -; LLG: 7; WGL: 12; SLE: 8; TT: 8
February | [10 empty] | WETS: -; WN: 2; FGY: 7; MYT: -; BDL: -; LLG: 3; WGL: 8; SLE: -; TT: 10
March | [10 empty] | WETS: -; WN: -; FGY: 9; MYT: -; BDL: -; LLG: 9; WGL: 12; SLE: 5; TT: 13
April | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 4
May | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 1; SLE: -; TT: 24
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | [10 empty] | WETS: -; WN: -; FGY: -; MYT: 1; BDL: -; LLG: 1; WGL: 4; SLE: -; TT: 8
August | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: 1; WGL: 7; SLE: -; TT: 9
September | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 7
October | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 1; SLE: -; TT: 7
November | [10 empty] | WETS: 9; WN: -; FGY: 8; MYT: -; BDL: -; LLG: 1; WGL: 8; SLE: -; TT: 11
December | [10 empty] | WETS: 11; WN: -; FGY: 3; MYT: -; BDL: -; LLG: -; WGL: 5; SLE: 2; TT: 9
Duration of Exceedance by Month Year 10 (number of consecuative hours on worst day) (hr)
January | [10 empty] | WETS: 21; WN: 7; FGY: 10; MYT: -; BDL: -; LLG: 7; WGL: 12; SLE: 8; TT: 8
February | [10 empty] | WETS: -; WN: 2; FGY: 7; MYT: -; BDL: -; LLG: 3; WGL: 8; SLE: -; TT: 10
March | [10 empty] | WETS: -; WN: -; FGY: 9; MYT: -; BDL: -; LLG: 9; WGL: 12; SLE: 5; TT: 13
April | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 4
May | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 1; SLE: -; TT: 24
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | [10 empty] | WETS: -; WN: -; FGY: -; MYT: 1; BDL: -; LLG: 1; WGL: 3; SLE: -; TT: 8
August | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: 1; WGL: 4; SLE: -; TT: 9
September | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 7
October | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 1; SLE: -; TT: 7
November | [10 empty] | WETS: 7; WN: -; FGY: 8; MYT: -; BDL: -; LLG: 1; WGL: 8; SLE: -; TT: 11
December | [10 empty] | WETS: 11; WN: -; FGY: 3; MYT: -; BDL: -; LLG: -; WGL: 5; SLE: 2; TT: 9
MAX EXCEEDANCE BY MONTH: Year 10 (MVA)
January | [10 empty] | WETS: 15.3; WN: 3.74; FGY: 12.5551; MYT: -; BDL: -; LLG: 5.5; WGL: 24.7836; SLE: 5.26; TT: 14.9651
February | [10 empty] | WETS: -; WN: 2.1089; FGY: 17.9597; MYT: -; BDL: -; LLG: 1.1034; WGL: 26.1389; SLE: -; TT: 30.0804
March | [10 empty] | WETS: -; WN: -; FGY: 20.68; MYT: -; BDL: -; LLG: 4.639; WGL: 30.58; SLE: 3.0905; TT: 30.14
April | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 1.6346; SLE: -; TT: 1.9135
May | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 4.4747; SLE: -; TT: 7.665
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | [10 empty] | WETS: -; WN: -; FGY: -; MYT: 1.1; BDL: -; LLG: 0.034537; WGL: 8.5802; SLE: -; TT: 13.6493
August | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: 0.33986; WGL: 11.2413; SLE: -; TT: 17.561
September | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 3.2631; SLE: -; TT: 8.5609
October | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 4.2425; SLE: -; TT: 8.5456
November | [10 empty] | WETS: 4.8779; WN: -; FGY: 15.8155; MYT: -; BDL: -; LLG: 0.51899; WGL: 20.454; SLE: -; TT: 25.5301
December | [10 empty] | WETS: 9.901; WN: -; FGY: 6.6579; MYT: -; BDL: -; LLG: -; WGL: 11.7467; SLE: 2.0564; TT: 28.1558
Number of days of Exceedance by Month: Year 10 (days)
January | [10 empty] | WETS: 20; WN: 3; FGY: 4; MYT: -; BDL: -; LLG: 4; WGL: 7; SLE: 2; TT: 10
February | [10 empty] | WETS: -; WN: 1; FGY: 6; MYT: -; BDL: -; LLG: 2; WGL: 10; SLE: -; TT: 17
March | [10 empty] | WETS: -; WN: -; FGY: 7; MYT: -; BDL: -; LLG: 2; WGL: 9; SLE: 4; TT: 12
April | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
May | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 2; SLE: -; TT: 11
June | bar: WETS; WN; FGY; MYT to WGL; SLE; TT
July | [10 empty] | WETS: -; WN: -; FGY: -; MYT: 2; BDL: -; LLG: 1; WGL: 22; SLE: -; TT: 22
August | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: 1; WGL: 15; SLE: -; TT: 22
September | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 4; SLE: -; TT: 9
October | [10 empty] | WETS: -; WN: -; FGY: -; MYT: -; BDL: -; LLG: -; WGL: 5; SLE: -; TT: 7
November | [10 empty] | WETS: 6; WN: -; FGY: 1; MYT: -; BDL: -; LLG: 1; WGL: 2; SLE: -; TT: 4
December | [10 empty] | WETS: 11; WN: -; FGY: 1; MYT: -; BDL: -; LLG: -; WGL: 4; SLE: 1; TT: 8
LOAD PROFILE: INVEST YEAR (MVA)
Year | 2017 |  | 2015 | 2016 |  | 2017 |  |  |  |  | 2021 | 2014 | 2018 | 2022 | 2018 | 2017 | 2014 |  |  |  | 2018 | 2014 | 2014 | 2015 | 2018 | 2019 | 2015 | 2016 | 2015 | 2019 | 2015 | 2015 |  | 2016 |  | 2015 | 2015 | 2019
Peak load (MVA) | 45.6 |  | 53 | 60.4 |  | 115.65 |  |  |  |  | 61 | 254.9 | 521 | 212.6222 | 44.24 | 39.2 | 51 |  |  |  | 71.08 | 28.7 | 18.9 | 52.7 | 20.4 | 67.86 | 25.3 | 64.5 | 30.1 | 25.22 | 49.9 | 28 |  | 55.6 |  | 106.1 | 94.8 | 88.88
Investment trigger point (MVA) | 44.9 |  | 47.4667 | 58.2 |  | 112.5 |  |  |  |  | 60.2 | 248.52 | 499.6667 | 209.1778 | 43.9 | 38.56 | 48.3 | 109 | 99 |  | 69.2 | 26.92 | 18.8 | 53.12 | 19.9 | 65.08 | 24.42 | 59.96 | 28.58 | 24.66 | 47.18 | 27.54 | 36.7 | 52.94 | 30.5 | 100.96 | 91.52 | 86.14
PEAK DAY LOAD PROFILE: INVEST YEAR (MVA)
12 am | [10 empty] | WETS: 38.6058; WN: 24.9845; FGY: 31.4418; MYT: 12.1911; BDL: 33.1014; LLG: 12.5111; WGL: 36.4134; SLE: 4.8453; TT: 33.0218
1 am | [10 empty] | WETS: 37.5422; WN: 23.4424; FGY: 27.5829; MYT: 14.9584; BDL: 32.8542; LLG: 11.6768; WGL: 34.4892; SLE: 4.5738; TT: 30.5093
2 am | [10 empty] | WETS: 41.3787; WN: 24.9613; FGY: 26.0346; MYT: 18.9; BDL: 36.1893; LLG: 12.6705; WGL: 36.2083; SLE: 4.6463; TT: 29.7381
3 am | [10 empty] | WETS: 45.6238; WN: 20.8422; FGY: 24.7707; MYT: 15.9166; BDL: 26.3086; LLG: 10.4909; WGL: 30.7546; SLE: 3.3991; TT: 29.5327
4 am | [10 empty] | WETS: 46.764; WN: 20.4659; FGY: 24.9923; MYT: 13.7315; BDL: 23.2703; LLG: 9.7729; WGL: 30.7034; SLE: 2.6299; TT: 32.2622
5 am | [10 empty] | WETS: 49.3004; WN: 21.1198; FGY: 28.8741; MYT: 12.5865; BDL: 23.2559; LLG: 9.7691; WGL: 31.9083; SLE: 3.5351; TT: 40.349
6 am | [10 empty] | WETS: 50.0836; WN: 24.6106; FGY: 35.9613; MYT: 11.9783; BDL: 26.15; LLG: 11.6085; WGL: 38.5978; SLE: 5.5437; TT: 52.1802
7 am | [10 empty] | WETS: 50.6534; WN: 31.4283; FGY: 40.3912; MYT: 11.2287; BDL: 28.4995; LLG: 12.3497; WGL: 42.7782; SLE: 7.597; TT: 66.2734
8 am | [10 empty] | WETS: 50.8162; WN: 33.2322; FGY: 44.1279; MYT: 9.7561; BDL: 30.4358; LLG: 11.6936; WGL: 41.374; SLE: 9.7458; TT: 72.1132
9 am | [10 empty] | WETS: 50.1078; WN: 34.7251; FGY: 47.4418; MYT: 10.7204; BDL: 35.2303; LLG: 11.7409; WGL: 42.6611; SLE: 11.2621; TT: 77.402
10 am | [10 empty] | WETS: 52.4769; WN: 37.1398; FGY: 50.055; MYT: 9.8638; BDL: 40.5782; LLG: 12.2269; WGL: 46.89; SLE: 15.2531; TT: 82.7117
11 am | [10 empty] | WETS: 55.3271; WN: 38.3877; FGY: 53.9806; MYT: 8.379; BDL: 44.6969; LLG: 12.9365; WGL: 50.6158; SLE: 22.7577; TT: 87.3982
12 pm | [10 empty] | WETS: 57.2331; WN: 39.6753; FGY: 56.8441; MYT: 7.5794; BDL: 47.7684; LLG: 13.597; WGL: 54.7413; SLE: 24.0786; TT: 87.9909
1 pm | [10 empty] | WETS: 58.0436; WN: 40.6972; FGY: 61.3178; MYT: 8.1722; BDL: 49.7452; LLG: 14.1159; WGL: 59.0105; SLE: 24.6938; TT: 88.88
2 pm | [10 empty] | WETS: 61; WN: 43.4736; FGY: 63.8218; MYT: 9.0026; BDL: 51.0117; LLG: 14.7474; WGL: 60.833; SLE: 28; TT: 87.1274
3 pm | [10 empty] | WETS: 60.5234; WN: 41.7174; FGY: 65.6746; MYT: 8.6266; BDL: 51.2872; LLG: 16.9734; WGL: 65.0655; SLE: 27.4986; TT: 84.0391
4 pm | [10 empty] | WETS: 54.7866; WN: 43.5392; FGY: 69.6761; MYT: 8.75; BDL: 49.7001; LLG: 18.7806; WGL: 67.86; SLE: 27.5489; TT: 81.5085
5 pm | [10 empty] | WETS: 53.4163; WN: 44.24; FGY: 71.08; MYT: 9.8633; BDL: 50.0273; LLG: 19.6756; WGL: 67.1716; SLE: 26.8747; TT: 72.6847
6 pm | [10 empty] | WETS: 52.3919; WN: 43.9835; FGY: 69.5934; MYT: 12.2671; BDL: 46.8214; LLG: 20.4; WGL: 64.0676; SLE: 26.5865; TT: 69.5254
7 pm | [10 empty] | WETS: 53.271; WN: 43.8197; FGY: 66.2432; MYT: 12.1796; BDL: 52.7; LLG: 19.5672; WGL: 61.6901; SLE: 24.2556; TT: 66.6828
8 pm | [10 empty] | WETS: 52.9008; WN: 40.9598; FGY: 62.5898; MYT: 11.1882; BDL: 50.0097; LLG: 18.0321; WGL: 55.0183; SLE: 21.3551; TT: 64.6412
9 pm | [10 empty] | WETS: 51.5046; WN: 36.4419; FGY: 54.4636; MYT: 9.3769; BDL: 46.2674; LLG: 16.2787; WGL: 47.0298; SLE: 18.7484; TT: 59.664
10 pm | [10 empty] | WETS: 51.2939; WN: 30.5178; FGY: 44.1351; MYT: 8.5893; BDL: 38.6901; LLG: 14.1335; WGL: 40.7302; SLE: 15.5865; TT: 48.7994
11 pm | [10 empty] | WETS: 53.7834; WN: 27.5304; FGY: 37.0199; MYT: 8.6072; BDL: 34.7666; LLG: 12.8813; WGL: 38.321; SLE: 13.992; TT: 43.9649
LOAD PROFILE: Year 10 (MVA)
Year | 2027 |  | 2025 | 2026 |  | 2027 |  |  |  |  | 2031 | 2024 | 2028 | 2032 | 2028 | 2027 | 2024 |  |  |  | 2028 | 2024 | 2024 | 2025 | 2028 | 2029 | 2025 | 2026 | 2025 | 2029 | 2025 | 2025 |  | 2026 |  | 2025 | 2025 | 2029
Peak load (MVA) | 52.6 |  | 108.3 | 82.4 |  | 147.15 |  |  |  |  | 75.5 | 319.55 | 712.3333 | 246.7889 | 47.64 | 45.6 | 87.5 |  |  |  | 89.88 | 52.1 | 19.9 | 44.1 | 25.4 | 95.66 | 35.5333 | 112.325 | 47.8667 | 30.82 | 78 | 32.8 |  | 81.15 |  | 164.6333 | 129.5333 | 116.28
Investment trigger point (MVA) | 44.9 |  | 47.4667 | 58.2 |  | 112.5 |  |  |  |  | 60.2 | 248.52 | 499.6667 | 209.1778 | 43.9 | 38.56 | 48.3 | 109 | 99 |  | 69.2 | 26.92 | 18.8 | 53.12 | 19.9 | 65.08 | 24.42 | 59.96 | 28.58 | 24.66 | 47.18 | 27.54 | 36.7 | 52.94 | 30.5 | 100.96 | 91.52 | 86.14
PEAK DAY LOAD PROFILE: Year 10 (MVA)
12 am | [10 empty] | WETS: 47.7826; WN: 26.9047; FGY: 39.7578; MYT: 12.8361; BDL: 27.6997; LLG: 15.5776; WGL: 51.3308; SLE: 5.6759; TT: 43.2018
1 am | [10 empty] | WETS: 46.4662; WN: 25.244; FGY: 34.8783; MYT: 15.7499; BDL: 27.4928; LLG: 14.5388; WGL: 48.6183; SLE: 5.3578; TT: 39.9147
2 am | [10 empty] | WETS: 51.2146; WN: 26.8797; FGY: 32.9206; MYT: 19.9; BDL: 30.2837; LLG: 15.7761; WGL: 51.0417; SLE: 5.4428; TT: 38.9058
3 am | [10 empty] | WETS: 56.4688; WN: 22.444; FGY: 31.3223; MYT: 16.7587; BDL: 22.0154; LLG: 13.0622; WGL: 43.3537; SLE: 3.9818; TT: 38.6371
4 am | [10 empty] | WETS: 57.88; WN: 22.0388; FGY: 31.6025; MYT: 14.458; BDL: 19.4729; LLG: 12.1683; WGL: 43.2815; SLE: 3.0807; TT: 42.208
5 am | [10 empty] | WETS: 61.0194; WN: 22.743; FGY: 36.5111; MYT: 13.2525; BDL: 19.4609; LLG: 12.1635; WGL: 44.9801; SLE: 4.1411; TT: 52.7878
6 am | [10 empty] | WETS: 61.9887; WN: 26.502; FGY: 45.4728; MYT: 12.6121; BDL: 21.8827; LLG: 14.4537; WGL: 54.41; SLE: 6.494; TT: 68.2663
7 am | [10 empty] | WETS: 62.6939; WN: 33.8437; FGY: 51.0743; MYT: 11.8228; BDL: 23.8488; LLG: 15.3766; WGL: 60.3029; SLE: 8.8994; TT: 86.7043
8 am | [10 empty] | WETS: 62.8955; WN: 35.7862; FGY: 55.7993; MYT: 10.2722; BDL: 25.4691; LLG: 14.5597; WGL: 58.3235; SLE: 11.4165; TT: 94.3443
9 am | [10 empty] | WETS: 62.0186; WN: 37.3939; FGY: 59.9897; MYT: 11.2876; BDL: 29.4812; LLG: 14.6186; WGL: 60.1379; SLE: 13.1927; TT: 101.2636
10 am | [10 empty] | WETS: 64.9509; WN: 39.9942; FGY: 63.2941; MYT: 10.3857; BDL: 33.9563; LLG: 15.2236; WGL: 66.0992; SLE: 17.8679; TT: 108.2101
11 am | [10 empty] | WETS: 68.4787; WN: 41.3379; FGY: 68.258; MYT: 8.8223; BDL: 37.4029; LLG: 16.1072; WGL: 71.3514; SLE: 26.6591; TT: 114.3414
12 pm | [10 empty] | WETS: 70.8377; WN: 42.7245; FGY: 71.8788; MYT: 7.9805; BDL: 39.9732; LLG: 16.9297; WGL: 77.1671; SLE: 28.2064; TT: 115.1168
1 pm | [10 empty] | WETS: 71.8409; WN: 43.825; FGY: 77.5358; MYT: 8.6046; BDL: 41.6273; LLG: 17.5757; WGL: 83.1851; SLE: 28.927; TT: 116.28
2 pm | [10 empty] | WETS: 75.5; WN: 46.8147; FGY: 80.7021; MYT: 9.4789; BDL: 42.6872; LLG: 18.3619; WGL: 85.7543; SLE: 32.8; TT: 113.9871
3 pm | [10 empty] | WETS: 74.9101; WN: 44.9235; FGY: 83.045; MYT: 9.0831; BDL: 42.9178; LLG: 21.1335; WGL: 91.7207; SLE: 32.2126; TT: 109.9468
4 pm | [10 empty] | WETS: 67.8096; WN: 46.8854; FGY: 88.1048; MYT: 9.213; BDL: 41.5897; LLG: 23.3837; WGL: 95.66; SLE: 32.2716; TT: 106.636
5 pm | [10 empty] | WETS: 66.1136; WN: 47.64; FGY: 89.88; MYT: 10.3852; BDL: 41.8635; LLG: 24.498; WGL: 94.6896; SLE: 31.4817; TT: 95.092
6 pm | [10 empty] | WETS: 64.8457; WN: 47.3638; FGY: 88.0002; MYT: 12.9161; BDL: 39.1807; LLG: 25.4; WGL: 90.314; SLE: 31.1442; TT: 90.9587
7 pm | [10 empty] | WETS: 65.9338; WN: 47.1874; FGY: 83.764; MYT: 12.8241; BDL: 44.1; LLG: 24.3631; WGL: 86.9625; SLE: 28.4138; TT: 87.2398
8 pm | [10 empty] | WETS: 65.4756; WN: 44.1077; FGY: 79.1442; MYT: 11.7802; BDL: 41.8488; LLG: 22.4518; WGL: 77.5575; SLE: 25.016; TT: 84.5688
9 pm | [10 empty] | WETS: 63.7475; WN: 39.2426; FGY: 68.8687; MYT: 9.873; BDL: 38.7172; LLG: 20.2686; WGL: 66.2963; SLE: 21.9624; TT: 78.0573
10 pm | [10 empty] | WETS: 63.4867; WN: 32.8632; FGY: 55.8085; MYT: 9.0438; BDL: 32.3763; LLG: 17.5976; WGL: 57.416; SLE: 18.2585; TT: 63.8434
11 pm | [10 empty] | WETS: 66.5679; WN: 29.6462; FGY: 46.8113; MYT: 9.0626; BDL: 29.0931; LLG: 16.0385; WGL: 54.0198; SLE: 16.3906; TT: 57.5185
SUMMER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 44.9 | 8 | 47.4667 | 58.2 |  | 112.5 | 117.1 |  | 101.7 | 109.9 | 77 | 350 | 509 | 341 | 66 | 40.5 | 66 | 109 | 99 |  | 93 | 27 | 20 | 48 | 33 | 84 | 33 | 66 | 26 | 27 | 40.5 | 39.5 | 40.5 | 54 | 39.5 | 99 | 93 | 84
n-1 capacity (MVA) | 44.9 | 8 | 47.4667 | 58.2 |  | 112.5 | 117.1 |  | 101.7 | 109.9 | - | 180 | 339 | 185 | 39.1 | 32.7 | 38.5 | 75 | 78.5 |  | 61.7 | 19.1 | 15 | 43.7 | 46.6 | 62.2 | - | 39.9 | 18.8 | 18.3 | 34.8 | 27.4 | 36.7 | 36.4 | 30.5 | 82.8 | 76.2 | 66.8
Secure capacity (MVA) | 44.9 | 8 | 47.4667 | 58.2 |  | 112.5 | 117.1 |  | 101.7 | 109.9 | 77 | 350 | 509 | 341 | 66 | 32.7 | 38.5 | 109 | 99 |  | 93 | 19.1 | 20 | 48 | 33 | 84 | 33 | 39.9 | 18.8 | 18.3 | 40.5 | 39.5 | 36.7 | 36.4 | 30.5 | 99 | 93 | 84
Reliability requirement | [14 empty] | n-1 | N-1 | N-1 | n-1 | n-1 |  | n-1 | N-1 | n-1 | n-1 | n-1 | n-1 |  | N-1 | N-1 | N-1 |  | n-1 | N-1 | N-1 | N-1 |  |  | n-1
Actual/forecast peak load: Summer (MVA)
2010 | 40.7 |  | 25.3333 | 47.2 |  | 93.6 |  |  |  |  | 43.1 | 228.84 | 347 | 170.9 | 41.52 | 34.72 | 36.4 | 52.42 | 48.92 |  | 56.04 | 19.34 | 13.54 | 57.44 | 14.12 | 42.84 | 20.04 | 35.32 | 20.96 | 20.18 | 35.76 | 25.58 | 30.16 | 40.48 | 27.56 | 76.12 | 77.24 | 64.22
2011 | 41.4 |  | 30.8667 | 49.4 |  | 96.75 |  |  |  |  | 45.2 | 235.22 | 370 | 174.4 | 47.5 | 36.5 | 51.2 | 66.6 | 69 |  | 69 | 25.2 | 13.2 | 56.8 | 18.4 | 48.7 | 18 | 46.4 | 26.3 | 21.9 | 48.5 | 23.9 | 34 | 49.9 | 28.8 | 85.4 | 84.3 | 75
2012 | 42.1 |  | 36.4 | 51.6 |  | 99.9 |  |  |  |  | 47.3 | 241.6 | 393 | 177.9 | 42.2 | 36 | 41.8 | 56.9 | 60 |  | 59.8 | 22.9 | 12.9 | 56.6 | 15.6 | 48.4 | 21.8 | 44.4 | 24 | 21.3 | 41.2 | 26.5 | 32 | 45.8 | 28.4 | 86.4 | 83.8 | 69.7
2013 | 42.8 |  | 42 | 53.4 |  | 102.2 |  |  |  |  | 51.4 | 248.2 | 431 | 180.8 | 42.2 | 38.1 | 49.9 | 65.1 | 73.7 |  | 67.9 | 27.7 | 11.1 | 51 | 17.7 | 55.5 | 23.6 | 57.3 | 28.6 | 22.5 | 43.4 | 27.2 | 34.3 | 52.2 | 30 | 101.4 | 89.7 | 77.9
2014 | 43.4 |  | 47.4 | 55.2 |  | 105.8 |  |  |  |  | 53.8 | 254.9 | 461 | 185 | 42.7 | 38.4 | 51 | 65.8 | 77.2 |  | 68.2 | 28.7 | 11.1 | 51.9 | 18.1 | 57.2 | 24.6 | 59.6 | 29.3 | 22.9 | 47.7 | 27.6 | 34.9 | 53.3 | 30.1 | 103.2 | 92.2 | 79.3
2015 | 44.1 |  | 53 | 57.5 |  | 109.2 |  |  |  |  | 55.4 | 261.3 | 477 | 188.5 | 43.1 | 38.7 | 52.1 | 66.6 | 80.7 |  | 68.5 | 29.7 | 11.2 | 52.7 | 18.5 | 58.9 | 25.3 | 62 | 30.1 | 23.3 | 49.9 | 28 | 35.4 | 54.5 | 30.2 | 106.1 | 94.8 | 80.6
2016 | 44.9 | 18.9 | 58.5 | 60.4 |  | 112.5 | 162.4 |  | 142.5 | 115.8 | 56.7 | 267.3 | 495 | 192.1 | 43.5 | 38.9 | 54.1 | 67.3 | 84.2 |  | 68.9 | 30.7 | 11.3 | 53.6 | 18.9 | 60.6 | 25.8 | 64.5 | 30.8 | 23.7 | 53.3 | 28.4 | 36 | 55.6 | 30.4 | 109 | 97.5 | 82
2017 | 45.6 |  | 64.0667 | 62.6 |  | 115.65 |  |  |  |  | 57.8 | 273.5 | 508 | 195.4 | 43.9 | 39.2 | 55.3 | 68.1 | 87.7 |  | 69.2 | 31.8 | 11.3 | 54.5 | 19.3 | 62.3 | 26.2 | 67.1 | 31.6 | 24.1 | 54.8 | 28.8 | 36.6 | 59.1 | 30.5 | 112.1 | 100.2 | 83.4
2018 | 46.3 |  | 69.6 | 64.8 |  | 118.8 |  |  |  |  | 58.6 | 279.8 | 521 | 199.4 | 44.24 | 39.84 | 59.9 | 70.34 | 93.24 |  | 71.08 | 34.7 | 10.4 | 53.2 | 20.04 | 65.08 | 27.3667 | 72.125 | 33.6333 | 24.66 | 57.7 | 29.3 | 37.52 | 61.55 | 30.92 | 118.6667 | 103.8667 | 86.14
2019 | 47 |  | 75.1333 | 67 |  | 121.95 |  |  |  |  | 59.4 | 286.2 | 535 | 201.9 | 44.58 | 40.48 | 64.5 | 72.58 | 98.78 |  | 72.96 | 37.6 | 9.5 | 51.9 | 20.78 | 67.86 | 28.5333 | 77.15 | 35.6667 | 25.22 | 60.6 | 29.8 | 38.44 | 64 | 31.34 | 125.2333 | 107.5333 | 88.88
2020 | 47.7 |  | 80.6667 | 69.2 |  | 125.1 |  |  |  |  | 60.2 | 292.8 | 548 | 205.4 | 44.92 | 41.12 | 69.1 | 74.82 | 104.32 |  | 74.84 | 40.5 | 8.6 | 50.6 | 21.52 | 70.64 | 29.7 | 82.175 | 37.7 | 25.78 | 63.5 | 30.3 | 39.36 | 66.45 | 31.76 | 131.8 | 111.2 | 91.62
2021 | 48.4 |  | 86.2 | 71.4 |  | 128.25 |  |  |  |  | 61 | 299.6 | 563 | 208.9 | 45.26 | 41.76 | 73.7 | 77.06 | 109.86 |  | 76.72 | 43.4 | 7.7 | 49.3 | 22.26 | 73.42 | 30.8667 | 87.2 | 39.7333 | 26.34 | 66.4 | 30.8 | 40.28 | 68.9 | 32.18 | 138.3667 | 114.8667 | 94.36
2022 | 49.1 |  | 91.7333 | 73.6 |  | 131.4 |  |  |  |  | 61.8 | 306.75 | 614.6667 | 212.6222 | 45.6 | 42.4 | 78.3 | 79.3 | 115.4 |  | 78.6 | 46.3 | 6.8 | 48 | 23 | 76.2 | 32.0333 | 92.225 | 41.7667 | 26.9 | 69.3 | 31.3 | 41.2 | 71.35 | 32.6 | 144.9333 | 118.5333 | 97.1
Average Growth (MVA/yr)
2012 to 2017 | 0.7 |  | 5.5333 | 2.2 |  | 3.15 |  |  |  |  | 2.1 | 6.38 | 23 | 3.5 | 0.34 | 0.64 | 2.7 | 2.24 | 5.54 |  | 1.88 | 1.78 | -0.32 | -0.42 | 0.74 | 2.78 | 0.88 | 4.54 | 1.52 | 0.56 | 2.72 | 0.46 | 0.92 | 2.66 | 0.42 | 5.14 | 3.28 | 2.74
2017 to 2022 | 0.7 |  | 5.5333 | 2.2 |  | 3.15 |  |  |  |  | 0.8 | 6.65 | 21.3333 | 3.4444 | 0.34 | 0.64 | 4.6 | 2.24 | 5.54 |  | 1.88 | 2.9 | -0.9 | -1.3 | 0.74 | 2.78 | 1.1667 | 5.025 | 2.0333 | 0.56 | 2.9 | 0.5 | 0.92 | 2.45 | 0.42 | 6.5667 | 3.6667 | 2.74
2022 onwards | 0.7 |  | 5.5333 | 2.2 |  | 3.15 |  |  |  |  | 1.5222 | 6.65 | 21.3333 | 3.4444 | 0.34 | 0.64 | 4.6 | 2.24 | 5.54 |  | 1.88 | 2.9 | -0.9 | -1.3 | 0.74 | 2.78 | 1.1667 | 5.025 | 2.0333 | 0.56 | 2.9 | 0.5 | 0.92 | 2.45 | 0.42 | 6.5667 | 3.6667 | 2.74
WINTER INPUTS
Nameplate capacity of transmission/distribution asset (MVA) | 760 |  | 330 | 435 |  | 828 |  |  |  |  | 77 | 350 | 509 | 341 | 40.3 | 40.5 | 66 |  |  |  | 56.65 | 27 | 18.8 | 50.3667 | 19.9 | 60.35 | 33 | 66 | 26 | 27 | 40.5 | 25.1 | 40.5 | 54 | 39.5 | 99 | 93 | 75.2
n-1 capacity (MVA) | 760 |  | 330 | -1 |  | -1 |  |  |  |  | - | 188 | 353 | 198 | 40.3 | 39.2 | 45.4 |  |  |  | 56.65 | 20.2 | 18.8 | 50.3667 | 19.9 | 60.35 | - | 43.8 | 20.2 | 20.2 | 38.6 | 25.1 | 40.4 | 41 | 30.5 | 92.2 | 76.2 | 75.2
Secure capacity (MVA) | 760 |  | 330 | 435 |  | 828 |  |  |  |  | 77 | 350 | 509 | 341 | 40.3 | 40.5 | 66 |  |  |  | 56.65 | 27 | 18.8 | 50.3667 | 19.9 | 60.35 | 33 | 66 | 26 | 27 | 40.5 | 25.1 | 40.5 | 54 | 39.5 | 99 | 93 | 75.2
Reliability requirement
Actual/forecast peak load: Winter (MVA)
2010 | 32.6 |  | 22.2333 | 27.7 |  | 78.15 |  |  |  |  | 15.38 | 169.26 | 255.8 | 164.06 | 37 | 27.7 | 35.28 | 48.2 | 53.5 |  | 59.1 | 19.2 | 22.9 | 52.8 | 18.9 | 45.4 | 8.18 | 32.26 | 16.48 | 18 | 35.04 | 21.6 | 29.9 | 37.36 | 23.76 | 65.24 | 60.72 | 61.9
2011 | 32.75 |  | 24.7667 | 28.7 |  | 81.375 |  |  |  |  | 18.34 | 172.78 | 272.4 | 167.38 | 38.3 | 30.3 | 35.7 | 51.4 | 45 |  | 56.2 | 22.4 | 23 | 47.8 | 18.4 | 45.9 | 12.6 | 36.9 | 16.5 | 17.7 | 42.4 | 23.6 | 24.6 | 38 | 24.7 | 60.5 | 65.4 | 63.3
2012 | 32.9 |  | 27.3 | 29.7 |  | 84.6 |  |  |  |  | 21.3 | 176.3 | 289 | 170.7 | 38.3 | 28.1 | 37.4 | 51.1 | 45.5 |  | 55.4 | 21.2 | 18.7 | 48.5 | 17.4 | 50 | 10.3 | 36.7 | 17.2 | 18.8 | 40.8 | 24.3 | 29.1 | 39.8 | 24 | 70 | 64.2 | 67.1
2013 | 33 |  | 30.3 | 30.8 |  | 86.6 |  |  |  |  | 31.9 | 180.4 | 322 | 174.3 | 38.8 | 28.5 | 39.3 | 52.2 | 48.4 |  | 55.5 | 22.8 | 18.8 | 49.6 | 18.2 | 52.1 | 13.7 | 40.6 | 17.9 | 19.5 | 42.7 | 24.8 | 25.7 | 40.7 | 24.2 | 74.4 | 65.3 | 68.8
2014 | 33.2 |  | 32.3 | 31.6 |  | 90.5 |  |  |  |  | 33.4 | 184.3 | 337 | 177.5 | 39.1 | 28.6 | 40 | 52.8 | 50.7 |  | 55.8 | 23.6 | 18.9 | 50.5 | 18.6 | 53.7 | 14.4 | 42.3 | 18.1 | 19.8 | 47.5 | 25.2 | 26 | 41.4 | 24.3 | 75.5 | 67.1 | 70
2015 | 33.3 |  | 34.9 | 32.5 |  | 92.4 |  |  |  |  | 34.4 | 187.2 | 349 | 180.7 | 39.5 | 28.8 | 40.6 | 53.4 | 53 |  | 56.1 | 24.5 | 19 | 51.3 | 19 | 55.3 | 14.9 | 44.1 | 18.4 | 20.1 | 49.9 | 25.5 | 26.4 | 42 | 24.4 | 77.5 | 69 | 71.2
2016 | 33.5 |  | 37.4 | 33.7 |  | 97.5 |  |  |  |  | 35.3 | 190.5 | 364 | 183.7 | 39.9 | 28.9 | 42 | 54 | 55.3 |  | 56.4 | 25.3 | 19.1 | 52.1 | 19.4 | 56.9 | 15.3 | 45.9 | 18.7 | 20.4 | 53.6 | 25.9 | 26.7 | 42.7 | 24.5 | 79.7 | 70.9 | 72.5
2017 | 33.65 |  | 39.9667 | 34.7 |  | 100.725 |  |  |  |  | 36.1 | 193.9 | 372 | 187.3 | 40.3 | 29.1 | 42.7 | 54.725 | 57.75 |  | 56.65 | 26.2 | 19.2 | 53.1667 | 19.9 | 58.625 | 15.6 | 47.8 | 19 | 20.8 | 55.2 | 26.3 | 27.1 | 45.9 | 24.6 | 81.9 | 72.9 | 73.85
2018 | 33.8 |  | 42.5 | 35.7 |  | 103.95 |  |  |  |  | 36.6 | 197.4 | 381 | 189.6 | 40.7 | 29.3 | 44 | 55.45 | 60.2 |  | 56.9 | 27.4 | 19.3 | 54.1 | 20.4 | 60.35 | 17.1333 | 50.1 | 19.4 | 21.2 | 58.2333 | 26.7 | 26.7 | 46.625 | 24.72 | 84.4 | 74.5 | 75.2
2019 | 33.95 |  | 45.0333 | 36.7 |  | 107.175 |  |  |  |  | 37.1 | 200.9 | 390 | 192.7 | 41.1 | 29.5 | 45.3 | 56.175 | 62.65 |  | 57.15 | 28.6 | 19.4 | 55.0333 | 20.9 | 62.075 | 18.6667 | 52.4 | 19.8 | 21.6 | 61.2667 | 27.1 | 26.3 | 47.35 | 24.84 | 86.9 | 76.1 | 76.55
2020 | 34.1 |  | 47.5667 | 37.7 |  | 110.4 |  |  |  |  | 37.6 | 204.5 | 399 | 195.8 | 41.5 | 29.7 | 46.6 | 56.9 | 65.1 |  | 57.4 | 29.8 | 19.5 | 55.9667 | 21.4 | 63.8 | 20.2 | 54.7 | 20.2 | 22 | 64.3 | 27.5 | 25.9 | 48.075 | 24.96 | 89.4 | 77.7 | 77.9
2021 | 34.25 |  | 50.1 | 38.7 |  | 113.625 |  |  |  |  | 38.2 | 208.1 | 409 | 198.7 | 41.9 | 29.9 | 47.9 | 57.625 | 67.55 |  | 57.65 | 31 | 19.6 | 56.9 | 21.9 | 65.525 | 21.7333 | 57 | 20.6 | 22.4 | 67.3333 | 27.9 | 25.5 | 48.8 | 25.08 | 91.9 | 79.3 | 79.25
2022 | 34.4 |  | 52.6333 | 39.7 |  | 116.85 |  |  |  |  | 38.7 | 213.9 | 448.6667 | 202.8556 | 42.3 | 30.1 | 49.2 | 58.35 | 70 |  | 57.9 | 32.2 | 19.7 | 57.8333 | 22.4 | 67.25 | 23.2667 | 59.3 | 21 | 22.8 | 70.3667 | 28.3 | 25.1 | 49.525 | 25.2 | 94.4 | 80.9 | 80.6
Average Growth (MVA/yr)
2012 to 2017 | 0.15 |  | 2.5333 | 1 |  | 3.225 |  |  |  |  | 2.96 | 3.52 | 16.6 | 3.32 | 0.4 | 0.2 | 1.06 | 0.725 | 2.45 |  | 0.25 | 1 | 0.1 | 0.93333 | 0.5 | 1.725 | 1.06 | 2.22 | 0.36 | 0.4 | 2.88 | 0.4 | -0.4 | 1.22 | 0.12 | 2.38 | 1.74 | 1.35
2017 to 2022 | 0.15 |  | 2.5333 | 1 |  | 3.225 |  |  |  |  | 0.52 | 4 | 15.3333 | 3.1111 | 0.4 | 0.2 | 1.3 | 0.725 | 2.45 |  | 0.25 | 1.2 | 0.1 | 0.93333 | 0.5 | 1.725 | 1.5333 | 2.3 | 0.4 | 0.4 | 3.0333 | 0.4 | -0.4 | 0.725 | 0.12 | 2.5 | 1.6 | 1.35
2022 onwards | 0.15 |  | 2.5333 | 1 |  | 3.225 |  |  |  |  | 1.8778 | 4 | 15.3333 | 3.1111 | 0.4 | 0.2 | 1.3 | 0.725 | 2.45 |  | 0.25 | 1.2 | 0.1 | 0.93333 | 0.5 | 1.725 | 1.5333 | 2.3 | 0.4 | 0.4 | 3.0333 | 0.4 | -0.4 | 0.725 | 0.12 | 2.5 | 1.6 | 1.35

## Default
GENERAL INPUTS
Display name of asset
Short name of asset
Full name of asset
Region
Asset type
Provider
Associated Tx
Associated STL
Latitude
Longitude
POE value
Season to use
Land available
Notes for outputsheet
Maximum connection
NETWORK INVESTMENT
Proposed investment ($m)
Proposed investment year
Annual Deferral Value of system in 2014 ($/kVA/yr)
Type of constraint
Constraint season
Capacity Shortfall: INVEST YEAR (MVA)
Capacity Shortfall: Year 10 (MVA)
SYSTEM INVESTMENT
Investment for system ($m)
Investment for ZS ($m)
Investment for Stli ($m)
Investment for TS ($m)
Investment year for system
Investment year for ZS
Investment year for Stli
Investment year for TS
System capacity shortfall: INVEST YEAR (MVA)
ZS capacity shortfall: INVEST YEAR (MVA)
Stli capacity shortfall: INVEST YEAR (MVA)
TS capacity shortfall: INVEST YEAR (MVA)
System capacity shortfall: Year 10 (MVA)
ZS capacity shortfall: Year 10 (MVA)
Stli capacity shortfall: Year 10 (MVA)
TS capacity shortfall: Year 10 (MVA)
NET PRESENT VALUE IN 2014 ($m)
of system
of asset
of linked ZS
of linked Stli
of linked TS
AVAILABLE CAPACITY (MVA)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
ANNUAL DEFERRAL VALUES or ADV
ADV OF Asset ($/kVA/year)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
ADV OF LINKED Stli ($/kVA/year)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
ADV OF LINKED TS ($/kVA/year)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
ADV OF SYSTEM ($/kVA/year)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
HOURLY EXCEEDANCES: INVEST YEAR
Investment trigger point (MVA)
Year
No. of hours over the trigger point (hr)
Duration of Exceedance by Month INVEST YEAR (total number of hours on worst day) (hr)
January
February
March
April
May
June
July
August
September
October
November
December
Duration of Exceedance by Month INVEST YEAR (number of consecuative hours on worst day) (hr)
January
February
March
April
May
June
July
August
September
October
November
December
MAX EXCEEDANCE BY MONTH: INVEST YEAR (MVA)
January
February
March
April
May
June
July
August
September
October
November
December
Number of days of Exceedance by Month: INVEST YEAR (days)
January
February
March
April
May
June
July
August
September
October
November
December
HOURLY EXCEEDANCES: Year 10
Investment trigger point (MVA)
Year
No. of hours over the trigger point (hr)
Duration of Exceedance by Month Year 10 (total number of hours on worst day) (hr)
January
February
March
April
May
June
July
August
September
October
November
December
Duration of Exceedance by Month Year 10 (number of consecuative hours on worst day) (hr)
January
February
March
April
May
June
July
August
September
October
November
December
MAX EXCEEDANCE BY MONTH: Year 10 (MVA)
January
February
March
April
May
June
July
August
September
October
November
December
Number of days of Exceedance by Month: Year 10 (days)
January
February
March
April
May
June
July
August
September
October
November
December
LOAD PROFILE: INVEST YEAR (MVA)
Year
Peak load (MVA)
Investment trigger point (MVA)
PEAK DAY LOAD PROFILE: INVEST YEAR (MVA)
12 am
1 am
2 am
3 am
4 am
5 am
6 am
7 am
8 am
9 am
10 am
11 am
12 pm
1 pm
2 pm
3 pm
4 pm
5 pm
6 pm
7 pm
8 pm
9 pm
10 pm
11 pm
LOAD PROFILE: Year 10 (MVA)
Year
Peak load (MVA)
Investment trigger point (MVA)
PEAK DAY LOAD PROFILE: Year 10 (MVA)
12 am
1 am
2 am
3 am
4 am
5 am
6 am
7 am
8 am
9 am
10 am
11 am
12 pm
1 pm
2 pm
3 pm
4 pm
5 pm
6 pm
7 pm
8 pm
9 pm
10 pm
11 pm
SUMMER INPUTS
Nameplate capacity of transmission/distribution asset (MVA)
n-1 capacity (MVA)
Secure capacity (MVA)
Reliability requirement
Actual/forecast peak load: Summer (MVA)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
Average Growth (MVA/yr)
2012 to 2017
2017 to 2022
2022 onwards
WINTER INPUTS
Nameplate capacity of transmission/distribution asset (MVA)
n-1 capacity (MVA)
Secure capacity (MVA)
Reliability requirement
Actual/forecast peak load: Winter (MVA)
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
Average Growth (MVA/yr)
2012 to 2017
2017 to 2022
2022 onwards

## Globals
Weighted Average Cost of Capital (WACC) (% p.a.)
| Vic | 0.064033
| Qld | 0.064033
| SA | 0.064033
| NSW | 0.064033
Year inputs
| Current Year | 2012
| Year for Dynamic Calculations | 2014
| First Year | 2010
| Final Year | 2022
| Discount Rate (% p.a.) | 0.07
| Depreciation Rate (% p.a.) | 0.025
| Number of additional years to be constrained as both | 2
| Year range is Calendar/Financial | Financial
| Number of years after investment NPV should calculate to | 10
Additional Transmission LRMC
| LRMC spread across network ($/kVA/yr in current yr) | -
Factors
| Winter to Summer adjustment factor | 0.9
| Summer to Winter adjustment factor | 0.9
| Do Worst Year Calaculation | True
Multiplier
| Powercor | 1
| SPAusnet | 1
| Ergon | 1
| SA Power Networks | 0.3
| Electranet | 1
| Essential | 1
| Transgrid | 1
Regions
| Vic | True
| Qld | True
| SA | True
| NSW | True